## System data
Base power (MW) | 1
Base voltage (KV) | 13.5
Upper bound for voltage (pu) | 1.05
Lower bound for voltage (pu) | 0.95
System power factor | 0.9
number of blocks of the piecewise linear energy losses | 3
Interest rate (%) | 10
Investment butget (106 $) | 3.5

## Operational Conditions
Maximun level of wind speed (m/s) | 17.08 | Operational Conditions Used for Scenario Generation (p.u.)
Maximun level of solar irradiation (W/m2) | 1114.21 | Time block | Average demand factor | Average wind speed factor | Average solar irradiation factor | duration (h)
Number of time blocks | 4 | 1 | 0.83340 | 0.50535 | 0.22026 | 350
Number of segments for demand | 3 (equiprobable) |  | 0.72168 | 0.32588 | 0.00000
Number of segments for wind spped | 3 (equiprobable) |  | 0.67027 | 0.17218 | 0.00000
Number of segments for solar irradiation | 3 (equiprobable) | 2 | 0.58940 | 0.49425 | 0.58421 | 2650
|  |  | 0.51504 | 0.31629 | 0.14816
|  |  | 0.47014 | 0.17309 | 0.00000
|  | 3 | 0.42664 | 0.51211 | 0.54507 | 3900
|  |  | 0.38973 | 0.31093 | 0.11964
|  |  | 0.35800 | 0.14763 | 0.00000
|  | 4 | 0.32606 | 0.53766 | 0.06212 | 1860
|  |  | 0.30166 | 0.29549 | 0.00000
|  |  | 0.27546 | 0.11993 | 0.00000
*it is assumed that all nodes are subjected to the same demand, wind speed, and solar irradiation profiles
**Three different conditions of demand, wind speed, and solar irradiation are considered. As a result, 27 equiprobable scenarios are generated for each time block, thereby totaling 108 scenarios for each stage.

## Peak Nodal Demands (MVA)
Peak Nodad Demands (MVA)
Node | Stage
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 2.05 | 2.1115 | 2.173 | 2.2345 | 2.296 | 2.3575 | 2.419 | 2.4805 | 2.542 | 2.6035
2 | 0.78 | 0.8034 | 0.8268 | 0.8502 | 0.8736 | 0.897 | 0.9204 | 0.9438 | 0.9672 | 0.9906
3 | 1.58 | 1.6274 | 1.6748 | 1.7222 | 1.7696 | 1.817 | 1.8644 | 1.9118 | 1.9592 | 2.0066
4 | 0.32 | 0.3296 | 0.3392 | 0.3488 | 0.3584 | 0.368 | 0.3776 | 0.3872 | 0.3968 | 0.4064
5 | 0.28 | 0.2884 | 0.2968 | 0.3052 | 0.3136 | 0.322 | 0.3304 | 0.3388 | 0.3472 | 0.3556
6 | 1.17 | 1.2051 | 1.2402 | 1.2753 | 1.3104 | 1.3455 | 1.3806 | 1.4157 | 1.4508 | 1.4859
7 | 1.24 | 1.2772 | 1.3144 | 1.3516 | 1.3888 | 1.426 | 1.4632 | 1.5004 | 1.5376 | 1.5748
8 | 0.72 | 0.7416 | 0.7632 | 0.7848 | 0.8064 | 0.828 | 0.8496 | 0.8712 | 0.8928 | 0.9144
9 | 1.14 | 1.1742 | 1.2084 | 1.2426 | 1.2768 | 1.311 | 1.3452 | 1.3794 | 1.4136 | 1.4478
10 | 1.56 | 1.6068 | 1.6536 | 1.7004 | 1.7472 | 1.794 | 1.8408 | 1.8876 | 1.9344 | 1.9812
11 | 1.91 | 1.9673 | 2.0246 | 2.0819 | 2.1392 | 2.1965 | 2.2538 | 2.3111 | 2.3684 | 2.4257
12 | 0.93 | 0.9579 | 0.9858 | 1.0137 | 1.0416 | 1.0695 | 1.0974 | 1.1253 | 1.1532 | 1.1811
13 | 1.15 | 1.1845 | 1.219 | 1.2535 | 1.288 | 1.3225 | 1.357 | 1.3915 | 1.426 | 1.4605
14 | 1.35 | 1.3905 | 1.431 | 1.4715 | 1.512 | 1.5525 | 1.593 | 1.6335 | 1.674 | 1.7145
15 | 1.62 | 1.6686 | 1.7172 | 1.7658 | 1.8144 | 1.863 | 1.9116 | 1.9602 | 2.0088 | 2.0574
16 | 2.16 | 2.2248 | 2.2896 | 2.3544 | 2.4192 | 2.484 | 2.5488 | 2.6136 | 2.6784 | 2.7432
17 | 1.4 | 1.442 | 1.484 | 1.526 | 1.568 | 1.61 | 1.652 | 1.694 | 1.736 | 1.778
18 | 2.1 | 2.163 | 2.226 | 2.289 | 2.352 | 2.415 | 2.478 | 2.541 | 2.604 | 2.667
19 | 1.81 | 1.8643 | 1.9186 | 1.9729 | 2.0272 | 2.0815 | 2.1358 | 2.1901 | 2.2444 | 2.2987
20 | 0 | 1.29 | 1.3287 | 1.3674 | 1.4061 | 1.4448 | 1.4835 | 1.5222 | 1.5609 | 1.5996
21 | 0 | 0.16 | 0.1648 | 0.1696 | 0.1744 | 0.1792 | 0.184 | 0.1888 | 0.1936 | 0.1984
22 | 0 | 1.63 | 1.6789 | 1.7278 | 1.7767 | 1.8256 | 1.8745 | 1.9234 | 1.9723 | 2.0212
23 | 0 | 0 | 0.34 | 0.3502 | 0.3604 | 0.3706 | 0.3808 | 0.391 | 0.4012 | 0.4114
24 | 0 | 0 | 2.51 | 2.5853 | 2.6606 | 2.7359 | 2.8112 | 2.8865 | 2.9618 | 3.0371
25 | 0 | 0 | 1.72 | 1.7716 | 1.8232 | 1.8748 | 1.9264 | 1.978 | 2.0296 | 2.0812
26 | 0 | 0 | 0 | 1.43 | 1.4729 | 1.5158 | 1.5587 | 1.6016 | 1.6445 | 1.6874
27 | 0 | 0 | 0 | 1.63 | 1.6789 | 1.7278 | 1.7767 | 1.8256 | 1.8745 | 1.9234
28 | 0 | 0 | 0 | 1.22 | 1.2566 | 1.2932 | 1.3298 | 1.3664 | 1.403 | 1.4396
29 | 0 | 0 | 0 | 0 | 0.16 | 0.1648 | 0.1696 | 0.1744 | 0.1792 | 0.184
30 | 0 | 0 | 0 | 0 | 1.35 | 1.3905 | 1.431 | 1.4715 | 1.512 | 1.5525
31 | 0 | 0 | 0 | 0 | 1.79 | 1.8437 | 1.8974 | 1.9511 | 2.0048 | 2.0585
32 | 0 | 0 | 0 | 0 | 0.23 | 0.2369 | 0.2438 | 0.2507 | 0.2576 | 0.2645
33 | 0 | 0 | 0 | 0 | 0 | 1.47 | 1.5141 | 1.5582 | 1.6023 | 1.6464
34 | 0 | 0 | 0 | 0 | 0 | 1.67 | 1.7201 | 1.7702 | 1.8203 | 1.8704
35 | 0 | 0 | 0 | 0 | 0 | 2.07 | 2.1321 | 2.1942 | 2.2563 | 2.3184
36 | 0 | 0 | 0 | 0 | 0 | 1.23 | 1.2669 | 1.3038 | 1.3407 | 1.3776
37 | 0 | 0 | 0 | 0 | 0 | 0 | 0.82 | 0.8446 | 0.8692 | 0.8938
38 | 0 | 0 | 0 | 0 | 0 | 0 | 1.71 | 1.7613 | 1.8126 | 1.8639
39 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | 0.2472 | 0.2544 | 0.2616
40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94 | 0.9682 | 0.9964
41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 1.339 | 1.378
42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.74 | 1.7922 | 1.8444
43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.09 | 1.1227 | 1.1554
44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44 | 0.4532
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.12 | 1.1536
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3 | 1.339
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.206
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.03
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.17
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.55

## d (hidden)
#BUS | NAME | TBUS | VM0 | VA0 | PD | QD | T1 | T2 | T3 | T4 | T5 | T6 | T7 | T8 | T9 | T10
# | [pu] | [rad] | [kVA] | [kVA] | [kVA] | [kVA] | 259 | 271.95 | 284.9 | 297.85 | 310.8 | 323.75 | 336.7 | 349.65 | 362.6 | 375.55
# | [6 empty] | 51.4225 | 53.9936 | 56.5647 | 59.1358 | 61.707 | 64.2781 | 66.8492 | 69.4203 | 71.9915 | 74.5626
201 | Bus 201(SS1) | 1 | 1 | 0 | 0 | 0 | 45.795 | 48.0847 | 50.3745 | 52.6642 | 54.954 | 57.2437 | 59.5335 | 61.8232 | 64.1129 | 66.4027
202 | Bus 202(SS2) | 1 | 1 | 0 | 0 | 0 | 93.6563 | 98.3392 | 103.022 | 107.7048 | 112.3876 | 117.0704 | 121.7533 | 126.4361 | 131.1189 | 135.8017
2 | Bus 2 | 0 | 1 | 0 | 0 | 0 | 335.0451 | 351.7973 | 368.5496 | 385.3019 | 402.0541 | 418.8064 | 435.5586 | 452.3109 | 469.0631 | 485.8154
3 | Bus 3 | 0 | 1 | 0 | 47.78 | 19.009 | 160.2193 | 168.2303 | 176.2413 | 184.2522 | 192.2632 | 200.2742 | 208.2851 | 216.2961 | 224.3071 | 232.318
4 | Bus 4 | 0 | 1 | 0 | 42.551 | 16.929 | 256.8657 | 269.709 | 282.5523 | 295.3956 | 308.2389 | 321.0822 | 333.9255 | 346.7688 | 359.612 | 372.4553
5 | Bus 5 | 0 | 1 | 0 | 87.022 | 34.622 | 67.0486 | 70.401 | 73.7534 | 77.1059 | 80.4583 | 83.8107 | 87.1631 | 90.5156 | 93.868 | 97.2204
6 | Bus 6 | 0 | 1 | 0 | 311.31 | 123.86 | 134.0893 | 140.7938 | 147.4983 | 154.2027 | 160.9072 | 167.6117 | 174.3161 | 181.0206 | 187.7251 | 194.4295
7 | Bus 7 | 0 | 1 | 0 | 148.87 | 59.228 | 150.8473 | 158.3896 | 165.932 | 173.4743 | 181.0167 | 188.5591 | 196.1014 | 203.6438 | 211.1862 | 218.7285
8 | Bus 8 | 0 | 1 | 0 | 238.67 | 94.956 | 125.7156 | 132.0014 | 138.2871 | 144.5729 | 150.8587 | 157.1445 | 163.4303 | 169.716 | 176.0018 | 182.2876
9 | Bus 9 | 0 | 1 | 0 | 62.299 | 24.786 | 268.1984 | 281.6083 | 295.0182 | 308.4281 | 321.8381 | 335.248 | 348.6579 | 362.0678 | 375.4777 | 388.8877
10 | Bus 10 | 0 | 1 | 0 | 124.59 | 49.571 | 313.5349 | 329.2117 | 344.8884 | 360.5652 | 376.2419 | 391.9187 | 407.5954 | 423.2722 | 438.9489 | 454.6256
11 | Bus 11 | 0 | 1 | 0 | 140.16 | 55.768 | 326.8763 | 343.2202 | 359.564 | 375.9078 | 392.2516 | 408.5954 | 424.9392 | 441.2831 | 457.6269 | 473.9707
12 | Bus 12 | 0 | 1 | 0 | 116.81 | 46.474 | 231.8113 | 243.4019 | 254.9924 | 266.583 | 278.1736 | 289.7641 | 301.3547 | 312.9453 | 324.5358 | 336.1264
13 | Bus 13 | 0 | 1 | 0 | 249.2 | 99.145 | 213.729 | 224.4155 | 235.1019 | 245.7884 | 256.4748 | 267.1613 | 277.8477 | 288.5342 | 299.2206 | 309.9071
14 | Bus 14 | 0 | 1 | 0 | 291.45 | 115.59 | 429 | 450.45 | 471.9 | 493.35 | 514.8 | 536.25 | 557.7 | 579.15 | 600.6 | 622.05
15 | Bus 15 | 0 | 1 | 0 | 303.72 | 120.84 | 158 | 165.9 | 173.8 | 181.7 | 189.6 | 197.5 | 205.4 | 213.3 | 221.2 | 229.1
16 | Bus 16 | 0 | 1 | 0 | 215.39 | 85.695 | 75 | 78.75 | 82.5 | 86.25 | 90 | 93.75 | 97.5 | 101.25 | 105 | 108.75
17 | Bus 17 | 0 | 1 | 0 | 198.59 | 79.007 | 33.5348 | 35.2115 | 36.8882 | 38.565 | 40.2417 | 41.9184 | 43.5952 | 45.2719 | 46.9487 | 48.6254
18 | Bus 18 | 0 | 1 | 0 | 0 | 0 | 257.0954 | 269.9502 | 282.805 | 295.6598 | 308.5145 | 321.3693 | 334.2241 | 347.0788 | 359.9336 | 372.7884
19 | Bus 19 | 0 | 1 | 0 | 0 | 0 | 67.0717 | 70.4253 | 73.7789 | 77.1325 | 80.4861 | 83.8397 | 87.1933 | 90.5468 | 93.9004 | 97.254
20 | Bus 20 | 0 | 1 | 0 | 0 | 0 | 257.0954 | 269.9502 | 282.805 | 295.6598 | 308.5145 | 321.3693 | 334.2241 | 347.0788 | 359.9336 | 372.7884
21 | Bus 21 | 0 | 1 | 0 | 30.127 | 14.729 | 134.1404 | 140.8474 | 147.5544 | 154.2614 | 160.9684 | 167.6755 | 174.3825 | 181.0895 | 187.7965 | 194.5035
22 | Bus 22 | 0 | 1 | 0 | 230.97 | 112.92 | 269 | 282.45 | 295.9 | 309.35 | 322.8 | 336.25 | 349.7 | 363.15 | 376.6 | 390.05
23 | Bus 23 | 0 | 1 | 0 | 60.256 | 29.459 | 63.4259 | 66.5972 | 69.7685 | 72.9398 | 76.1111 | 79.2824 | 82.4537 | 85.625 | 88.7963 | 91.9676
24 | Bus 24 | 0 | 1 | 0 | 230.97 | 112.92 | 405.9162 | 426.212 | 446.5078 | 466.8036 | 487.0994 | 507.3953 | 527.6911 | 547.9869 | 568.2827 | 588.5785
25 | Bus 25 | 0 | 1 | 0 | 120.51 | 58.915 | 216 | 226.8 | 237.6 | 248.4 | 259.2 | 270 | 280.8 | 291.6 | 302.4 | 313.2
26 | Bus 26 | 0 | 1 | 0 | 0 | 0 | 138.7486 | 145.6861 | 152.6235 | 159.5609 | 166.4984 | 173.4358 | 180.3732 | 187.3107 | 194.2481 | 201.1855
27 | Bus 27 | 0 | 1 | 0 | 56.981 | 27.857 | 63.4259 | 66.5972 | 69.7685 | 72.9398 | 76.1111 | 79.2824 | 82.4537 | 85.625 | 88.7963 | 91.9676
28 | Bus 28 | 0 | 1 | 0 | 364.67 | 178.28 | 377 | 395.85 | 414.7 | 433.55 | 452.4 | 471.25 | 490.1 | 508.95 | 527.8 | 546.65
29 | Bus 29 | 0 | 1 | 0 | 0 | 0 | 95.1409 | 99.8979 | 104.655 | 109.412 | 114.1691 | 118.9261 | 123.6831 | 128.4402 | 133.1972 | 137.9543
30 | Bus 30 | 0 | 1 | 0 | 124.65 | 60.939 | 171 | 179.55 | 188.1 | 196.65 | 205.2 | 213.75 | 222.3 | 230.85 | 239.4 | 247.95
31 | Bus 31 | 0 | 1 | 0 | 56.981 | 27.857 | 441.6142 | 463.6949 | 485.7756 | 507.8563 | 529.9371 | 552.0178 | 574.0985 | 596.1792 | 618.2599 | 640.3406
32 | Bus 32 | 0 | 1 | 0 | 0 | 0 | 373 | 391.65 | 410.3 | 428.95 | 447.6 | 466.25 | 484.9 | 503.55 | 522.2 | 540.85
33 | Bus 33 | 0 | 1 | 0 | 85.473 | 41.787 | 201.6401 | 211.7221 | 221.8041 | 231.8861 | 241.9681 | 252.0501 | 262.1321 | 272.2141 | 282.2961 | 292.3781
34 | Bus 34 | 0 | 1 | 0 | 0 | 0 | 269.5598 | 283.0378 | 296.5158 | 309.9938 | 323.4718 | 336.9498 | 350.4278 | 363.9058 | 377.3838 | 390.8618
35 | Bus 35 | 0 | 1 | 0 | 396.74 | 193.96 | 83.8349 | 88.0266 | 92.2184 | 96.4101 | 100.6018 | 104.7936 | 108.9853 | 113.1771 | 117.3688 | 121.5606
36 | Bus 36 | 0 | 1 | 0 | 0 | 0 | 143 | 150.15 | 157.3 | 164.45 | 171.6 | 178.75 | 185.9 | 193.05 | 200.2 | 207.35
37 | Bus 37 | 0 | 1 | 0 | 181.15 | 88.563 | 1.3618 | 1.4299 | 1.498 | 1.5661 | 1.6342 | 1.7022 | 1.7703 | 1.8384 | 1.9065 | 1.9746
38 | Bus 38 | 0 | 1 | 0 | 242.17 | 118.39 | 6.8146 | 7.1553 | 7.4961 | 7.8368 | 8.1775 | 8.5182 | 8.859 | 9.1997 | 9.5404 | 9.8812
39 | Bus 39 | 0 | 1 | 0 | 75.316 | 36.821 | 171 | 179.55 | 188.1 | 196.65 | 205.2 | 213.75 | 222.3 | 230.85 | 239.4 | 247.95
40 | Bus 40 | 0 | 1 | 0 | 0 | 0 | 128.0344 | 134.4361 | 140.8378 | 147.2395 | 153.6412 | 160.0429 | 166.4447 | 172.8464 | 179.2481 | 185.6498
41 | Bus 41 | 0 | 1 | 0 | 1.254 | 0.531 | 67.6823 | 71.0665 | 74.4506 | 77.8347 | 81.2188 | 84.6029 | 87.987 | 91.3712 | 94.7553 | 98.1394
42 | Bus 42 | 0 | 1 | 0 | 6.274 | 2.66 | 187.1305 | 196.487 | 205.8435 | 215.2 | 224.5566 | 233.9131 | 243.2696 | 252.6261 | 261.9826 | 271.3392
43 | Bus 43 | 0 | 1 | 0 | 0 | 0 | 498.061 | 522.964 | 547.8671 | 572.7701 | 597.6732 | 622.5762 | 647.4793 | 672.3823 | 697.2854 | 722.1884
44 | Bus 44 | 0 | 1 | 0 | 117.88 | 49.971 | 285.6108 | 299.8913 | 314.1719 | 328.4524 | 342.7329 | 357.0135 | 371.294 | 385.5746 | 399.8551 | 414.1356
45 | Bus 45 | 0 | 1 | 0 | 62.668 | 25.566 | 256.0687 | 268.8721 | 281.6756 | 294.479 | 307.2824 | 320.0859 | 332.8893 | 345.6927 | 358.4962 | 371.2996
46 | Bus 46 | 0 | 1 | 0 | 172.29 | 73.034 | 204 | 214.2 | 224.4 | 234.6 | 244.8 | 255 | 265.2 | 275.4 | 285.6 | 295.8
47 | Bus 47 | 0 | 1 | 0 | 458.56 | 194.39 | 118.6276 | 124.559 | 130.4904 | 136.4218 | 142.3531 | 148.2845 | 154.2159 | 160.1473 | 166.0787 | 172.0101
48 | Bus 48 | 0 | 1 | 0 | 262.96 | 111.47 | 289 | 303.45 | 317.9 | 332.35 | 346.8 | 361.25 | 375.7 | 390.15 | 404.6 | 419.05
49 | Bus 49 | 0 | 1 | 0 | 235.76 | 99.942 | 79.081 | 83.035 | 86.9891 | 90.9431 | 94.8972 | 98.8512 | 102.8053 | 106.7593 | 110.7133 | 114.6674
50 | Bus 50 | 0 | 1 | 0 | 0 | 0 | 280.7353 | 294.7721 | 308.8089 | 322.8456 | 336.8824 | 350.9192 | 364.9559 | 378.9927 | 393.0295 | 407.0662
51 | Bus 51 | 0 | 1 | 0 | 109.22 | 46.298 | 75.1274 | 78.8838 | 82.6402 | 86.3965 | 90.1529 | 93.9093 | 97.6657 | 101.422 | 105.1784 | 108.9348
52 | Bus 52 | 0 | 1 | 0 | 0 | 0 | 23.7248 | 24.911 | 26.0972 | 27.2835 | 28.4697 | 29.656 | 30.8422 | 32.0284 | 33.2147 | 34.4009
53 | Bus 53 | 0 | 1 | 0 | 72.809 | 30.865 | 442 | 464.1 | 486.2 | 508.3 | 530.4 | 552.5 | 574.6 | 596.7 | 618.8 | 640.9
54 | Bus 54 | 0 | 1 | 0 | 258.47 | 109.57 | 22.2953 | 23.4101 | 24.5249 | 25.6396 | 26.7544 | 27.8692 | 28.984 | 30.0987 | 31.2135 | 32.3283
55 | Bus 55 | 0 | 1 | 0 | 69.169 | 29.322 | 163.5181 | 171.694 | 179.8699 | 188.0458 | 196.2217 | 204.3976 | 212.5735 | 220.7494 | 228.9253 | 237.1012
56 | Bus 56 | 0 | 1 | 0 | 21.843 | 9.26 | 239.6999 | 251.6849 | 263.6699 | 275.6549 | 287.6399 | 299.6249 | 311.6099 | 323.5949 | 335.5799 | 347.5649
57 | Bus 57 | 0 | 1 | 0 | 0 | 0 | 100.3421 | 105.3592 | 110.3763 | 115.3935 | 120.4106 | 125.4277 | 130.4448 | 135.4619 | 140.479 | 145.4961
58 | Bus 58 | 0 | 1 | 0 | 20.527 | 8.702 | 425 | 446.25 | 467.5 | 488.75 | 510 | 531.25 | 552.5 | 573.75 | 595 | 616.25
59 | Bus 59 | 0 | 1 | 0 | 150.55 | 63.819 | 246.2178 | 258.5286 | 270.8395 | 283.1504 | 295.4613 | 307.7722 | 320.0831 | 332.394 | 344.7049 | 357.0157
60 | Bus 60 | 0 | 1 | 0 | 220.69 | 93.552 | 365 | 383.25 | 401.5 | 419.75 | 438 | 456.25 | 474.5 | 492.75 | 511 | 529.25
61 | Bus 61 | 0 | 1 | 0 | 92.384 | 39.163 | 316.4328 | 332.2545 | 348.0761 | 363.8978 | 379.7194 | 395.541 | 411.3627 | 427.1843 | 443.006 | 458.8276
62 | Bus 62 | 0 | 1 | 0 | 0 | 0 | 89.3439 | 93.8111 | 98.2783 | 102.7455 | 107.2127 | 111.6799 | 116.1471 | 120.6143 | 125.0815 | 129.5487
63 | Bus 63 | 0 | 1 | 0 | 226.69 | 96.098 | 89.3439 | 93.8111 | 98.2783 | 102.7455 | 107.2127 | 111.6799 | 116.1471 | 120.6143 | 125.0815 | 129.5487
64 | Bus 64 | 0 | 1 | 0 | 0 | 0 | 111.6811 | 117.2651 | 122.8492 | 128.4332 | 134.0173 | 139.6014 | 145.1854 | 150.7695 | 156.3535 | 161.9376
65 | Bus 65 | 0 | 1 | 0 | 294.02 | 116.97 | 189.8586 | 199.3515 | 208.8444 | 218.3374 | 227.8303 | 237.3232 | 246.8162 | 256.3091 | 265.802 | 275.2949
66 | Bus 66 | 0 | 1 | 0 | 83.015 | 33.028 | 89.3439 | 93.8111 | 98.2783 | 102.7455 | 107.2127 | 111.6799 | 116.1471 | 120.6143 | 125.0815 | 129.5487
67 | Bus 67 | 0 | 1 | 0 | 83.015 | 33.028 | 234.5329 | 246.2595 | 257.9862 | 269.7128 | 281.4395 | 293.1661 | 304.8927 | 316.6194 | 328.346 | 340.0727
68 | Bus 68 | 0 | 1 | 0 | 103.77 | 41.285 | 25.0697 | 26.3231 | 27.5766 | 28.8301 | 30.0836 | 31.3371 | 32.5906 | 33.844 | 35.0975 | 36.351
69 | Bus 69 | 0 | 1 | 0 | 176.41 | 70.184 | 5.4619 | 5.735 | 6.0081 | 6.2811 | 6.5542 | 6.8273 | 7.1004 | 7.3735 | 7.6466 | 7.9197
70 | Bus 70 | 0 | 1 | 0 | 83.015 | 33.028 | 78.1756 | 82.0844 | 85.9932 | 89.902 | 93.8108 | 97.7196 | 101.6283 | 105.5371 | 109.4459 | 113.3547
71 | Bus 71 | 0 | 1 | 0 | 217.92 | 86.698 | 436.94 | 458.787 | 480.634 | 502.481 | 524.328 | 546.175 | 568.022 | 589.869 | 611.716 | 633.563
72 | Bus 72 | 0 | 1 | 0 | 23.294 | 9.267 | 185 | 194.25 | 203.5 | 212.75 | 222 | 231.25 | 240.5 | 249.75 | 259 | 268.25
73 | Bus 73 | 0 | 1 | 0 | 5.075 | 2.019 | 108.8098 | 114.2502 | 119.6907 | 125.1312 | 130.5717 | 136.0122 | 141.4527 | 146.8932 | 152.3337 | 157.7741
74 | Bus 74 | 0 | 1 | 0 | 72.638 | 28.899 | 154.7972 | 162.537 | 170.2769 | 178.0167 | 185.7566 | 193.4965 | 201.2363 | 208.9762 | 216.716 | 224.4559
75 | Bus 75 | 0 | 1 | 0 | 405.99 | 161.52 | 104.315 | 109.5307 | 114.7465 | 119.9622 | 125.178 | 130.3937 | 135.6095 | 140.8252 | 146.041 | 151.2567
76 | Bus 76 | 0 | 1 | 0 | 0 | 0 | 326.3331 | 342.6498 | 358.9665 | 375.2831 | 391.5998 | 407.9164 | 424.2331 | 440.5497 | 456.8664 | 473.1831
77 | Bus 77 | 0 | 1 | 0 | 100.18 | 42.468 | 153.4064 | 161.0767 | 168.747 | 176.4173 | 184.0876 | 191.758 | 199.4283 | 207.0986 | 214.7689 | 222.4392
78 | Bus 78 | 0 | 1 | 0 | 142.52 | 60.417 | 303.9558 | 319.1535 | 334.3513 | 349.5491 | 364.7469 | 379.9447 | 395.1425 | 410.3403 | 425.5381 | 440.7358
79 | Bus 79 | 0 | 1 | 0 | 96.042 | 40.713 | 94.8333 | 99.5749 | 104.3166 | 109.0583 | 113.7999 | 118.5416 | 123.2832 | 128.0249 | 132.7666 | 137.5082
80 | Bus 80 | 0 | 1 | 0 | 300.45 | 127.37 | 264.855 | 278.0978 | 291.3405 | 304.5833 | 317.826 | 331.0688 | 344.3115 | 357.5543 | 370.797 | 384.0398
81 | Bus 81 | 0 | 1 | 0 | 141.24 | 59.873 | 269.0936 | 282.5483 | 296.003 | 309.4576 | 322.9123 | 336.367 | 349.8217 | 363.2764 | 376.731 | 390.1857
82 | Bus 82 | 0 | 1 | 0 | 279.85 | 118.63 | 424 | 445.2 | 466.4 | 487.6 | 508.8 | 530 | 551.2 | 572.4 | 593.6 | 614.8
83 | Bus 83 | 0 | 1 | 0 | 87.312 | 37.013 | 97.6204 | 102.5014 | 107.3824 | 112.2635 | 117.1445 | 122.0255 | 126.9065 | 131.7875 | 136.6685 | 141.5496
84 | Bus 84 | 0 | 1 | 0 | 243.85 | 103.37 | 1235.2657 | 1297.029 | 1358.7923 | 1420.5556 | 1482.3188 | 1544.0821 | 1605.8454 | 1667.6087 | 1729.372 | 1791.1353
85 | Bus 85 | 0 | 1 | 0 | 247.75 | 105.03 | 497.8233 | 522.7145 | 547.6056 | 572.4968 | 597.388 | 622.2791 | 647.1703 | 672.0615 | 696.9526 | 721.8438
86 | Bus 86 | 0 | 1 | 0 | 0 | 0 | 418.381 | 439.3001 | 460.2191 | 481.1382 | 502.0572 | 522.9763 | 543.8953 | 564.8144 | 585.7334 | 606.6525
87 | Bus 87 | 0 | 1 | 0 | 89.878 | 38.101 | 67 | 70.35 | 73.7 | 77.05 | 80.4 | 83.75 | 87.1 | 90.45 | 93.8 | 97.15
88 | Bus 88 | 0 | 1 | 0 | 1137.3 | 482.11 | 86.4656 | 90.7888 | 95.1121 | 99.4354 | 103.7587 | 108.082 | 112.4052 | 116.7285 | 121.0518 | 125.3751
89 | Bus 89 | 0 | 1 | 0 | 458.34 | 194.3 | 94.8333 | 99.5749 | 104.3166 | 109.0583 | 113.7999 | 118.5416 | 123.2832 | 128.0249 | 132.7666 | 137.5082
90 | Bus 90 | 0 | 1 | 0 | 385.2 | 163.29 | 260 | 273 | 286 | 299 | 312 | 325 | 338 | 351 | 364 | 377
91 | Bus 91 | 0 | 1 | 0 | 0 | 0 | 80.3755 | 84.3943 | 88.4131 | 92.4319 | 96.4506 | 100.4694 | 104.4882 | 108.507 | 112.5257 | 116.5445
92 | Bus 92 | 0 | 1 | 0 | 79.608 | 33.747 | 252.039 | 264.641 | 277.2429 | 289.8449 | 302.4468 | 315.0488 | 327.6507 | 340.2527 | 352.8546 | 365.4566
93 | Bus 93 | 0 | 1 | 0 | 87.312 | 37.013 | 154.0364 | 161.7382 | 169.44 | 177.1418 | 184.8437 | 192.5455 | 200.2473 | 207.9491 | 215.6509 | 223.3528
94 | Bus 94 | 0 | 1 | 0 | 0 | 0 | 67 | 70.35 | 73.7 | 77.05 | 80.4 | 83.75 | 87.1 | 90.45 | 93.8 | 97.15
95 | Bus 95 | 0 | 1 | 0 | 74.001 | 31.37 | 83.0345 | 87.1862 | 91.3379 | 95.4897 | 99.6414 | 103.7931 | 107.9448 | 112.0966 | 116.2483 | 120.4
96 | Bus 96 | 0 | 1 | 0 | 232.05 | 98.369 | 363 | 381.15 | 399.3 | 417.45 | 435.6 | 453.75 | 471.9 | 490.05 | 508.2 | 526.35
97 | Bus 97 | 0 | 1 | 0 | 141.82 | 60.119 | 55.7429 | 58.53 | 61.3172 | 64.1043 | 66.8915 | 69.6786 | 72.4658 | 75.2529 | 78.0401 | 80.8272
98 | Bus 98 | 0 | 1 | 0 | 0 | 0 | 65.0315 | 68.283 | 71.5346 | 74.7862 | 78.0378 | 81.2893 | 84.5409 | 87.7925 | 91.044 | 94.2956
99 | Bus 99 | 0 | 1 | 0 | 76.449 | 32.408 | 130 | 136.5 | 143 | 149.5 | 156 | 162.5 | 169 | 175.5 | 182 | 188.5
100 | Bus 100 | 0 | 1 | 0 | 0 | 0 | 224 | 235.2 | 246.4 | 257.6 | 268.8 | 280 | 291.2 | 302.4 | 313.6 | 324.8
101 | Bus 101 | 0 | 1 | 0 | 51.322 | 21.756 | 0 | 18.1765 | 19.0853 | 19.9941 | 20.903 | 21.8118 | 22.7206 | 23.6294 | 24.5383 | 25.4471
102 | Bus 102 | 0 | 1 | 0 | 59.874 | 25.381 | 0 | 1636.2734 | 1718.087 | 1799.9007 | 1881.7144 | 1963.528 | 2045.3417 | 2127.1554 | 2208.969 | 2290.7827
103 | Bus 103 | 0 | 1 | 0 | 9.065 | 3.843 | 0 | 339.9826 | 356.9817 | 373.9808 | 390.98 | 407.9791 | 424.9782 | 441.9774 | 458.9765 | 475.9756
104 | Bus 104 | 0 | 1 | 0 | 2.092 | 0.887 | 0 | 86.708 | 91.0434 | 95.3788 | 99.7141 | 104.0495 | 108.3849 | 112.7203 | 117.0557 | 121.3911
105 | Bus 105 | 0 | 1 | 0 | 16.735 | 7.094 | 0 | 0 | 55.7429 | 58.53 | 61.3172 | 64.1043 | 66.8915 | 69.6786 | 72.4658 | 75.2529
106 | Bus 106 | 0 | 1 | 0 | 1506.5 | 638.63 | 0 | 0 | 73 | 76.65 | 80.3 | 83.95 | 87.6 | 91.25 | 94.9 | 98.55
107 | Bus 107 | 0 | 1 | 0 | 313.02 | 132.69 | 0 | 0 | 219.8776 | 230.8715 | 241.8654 | 252.8593 | 263.8531 | 274.847 | 285.8409 | 296.8348
108 | Bus 108 | 0 | 1 | 0 | 79.831 | 33.842 | 0 | 0 | 0 | 66.0977 | 69.4025 | 72.7074 | 76.0123 | 79.3172 | 82.6221 | 85.927
109 | Bus 109 | 0 | 1 | 0 | 51.322 | 21.756 | 0 | 0 | 0 | 49.5476 | 52.0249 | 54.5023 | 56.9797 | 59.4571 | 61.9344 | 64.4118
110 | Bus 110 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 152 | 159.6 | 167.2 | 174.8 | 182.4 | 190 | 197.6
111 | Bus 111 | 0 | 1 | 0 | 202.44 | 85.815 | 0 | 0 | 0 | 170.6002 | 179.1302 | 187.6602 | 196.1902 | 204.7202 | 213.2502 | 221.7802
112 | Bus 112 | 0 | 1 | 0 | 60.823 | 25.874 | 0 | 0 | 0 | 0 | 117 | 122.85 | 128.7 | 134.55 | 140.4 | 146.25
113 | Bus 113 | 0 | 1 | 0 | 45.618 | 19.338 | 0 | 0 | 0 | 0 | 271.6974 | 285.2823 | 298.8672 | 312.4521 | 326.0369 | 339.6218
114 | Bus 114 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 355 | 372.75 | 390.5 | 408.25 | 426 | 443.75
115 | Bus 115 | 0 | 1 | 0 | 157.07 | 66.584 | 0 | 0 | 0 | 0 | 74.5133 | 78.239 | 81.9647 | 85.6903 | 89.416 | 93.1417
116 | Bus 116 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34.8348 | 36.5766 | 38.3183 | 40.06 | 41.8018
117 | Bus 117 | 0 | 1 | 0 | 250.15 | 106.04 | 0 | 0 | 0 | 0 | 0 | 66.3457 | 69.663 | 72.9803 | 76.2976 | 79.6149
118 | Bus 118 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 286.65 | 300.3 | 313.95 | 327.6
119 | Bus 119 | 0 | 1 | 0 | 68.809 | 28.593 | 0 | 0 | 0 | 0 | 0 | 0 | 105.3248 | 110.591 | 115.8573 | 121.1235
120 | Bus 120 | 0 | 1 | 0 | 32.072 | 13.596 | 0 | 0 | 0 | 0 | 0 | 0 | 55.4974 | 58.2723 | 61.0471 | 63.822
121 | Bus 121 | 0 | 1 | 0 | 61.084 | 25.894 | 0 | 0 | 0 | 0 | 0 | 0 | 137.0916 | 143.9462 | 150.8008 | 157.6554
122 | Bus 122 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2119 | 91.5725 | 95.9331 | 100.2937
123 | Bus 123 | 0 | 1 | 0 | 94.622 | 46.26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.934 | 170.0307 | 178.1274
124 | Bus 124 | 0 | 1 | 0 | 49.858 | 24.375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.786 | 24.9753 | 26.1646
125 | Bus 125 | 0 | 1 | 0 | 123.16 | 60.214 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.2485 | 87.411 | 91.5734
126 | Bus 126 | 0 | 1 | 0 | 78.35 | 38.304 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.7099 | 266.3954
127 | Bus 127 | 0 | 1 | 0 | 145.48 | 71.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 39.6421 | 41.6243
128 | Bus 128 | 0 | 1 | 0 | 21.369 | 10.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277.4892 | 291.3636
129 | Bus 129 | 0 | 1 | 0 | 74.789 | 36.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352.5436
130 | Bus 130 | 0 | 1 | 0 | 227.93 | 111.43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 371.5778
131 | Bus 131 | 0 | 1 | 0 | 35.614 | 17.411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 277.4892
132 | Bus 132 | 0 | 1 | 0 | 249.29 | 121.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317
133 | Bus 133 | 0 | 1 | 0 | 316.72 | 154.84
134 | Bus 134 | 0 | 1 | 0 | 333.82 | 163.2
135 | Bus 135 | 0 | 1 | 0 | 249.29 | 121.88
136 | Bus 136 | 0 | 1 | 0 | 0 | 0

## Numbers of customers per node
Numbers of Customers per Node
Node | Stage
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 242 | 246 | 249 | 253 | 257 | 260 | 264 | 268 | 271 | 275
2 | 165 | 166 | 168 | 169 | 170 | 172 | 173 | 174 | 176 | 177
3 | 194 | 196 | 198 | 201 | 203 | 205 | 207 | 210 | 212 | 214
4 | 200 | 202 | 205 | 207 | 210 | 212 | 214 | 217 | 219 | 222
5 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 164 | 165 | 166
6 | 194 | 196 | 198 | 201 | 203 | 205 | 207 | 210 | 212 | 214
7 | 257 | 261 | 265 | 269 | 273 | 278 | 282 | 286 | 290 | 294
8 | 263 | 267 | 272 | 276 | 280 | 284 | 289 | 293 | 297 | 302
9 | 160 | 161 | 162 | 164 | 165 | 166 | 167 | 168 | 170 | 171
10 | 245 | 249 | 253 | 256 | 260 | 264 | 268 | 271 | 275 | 279
11 | 189 | 191 | 193 | 195 | 197 | 199 | 201 | 203 | 206 | 208
12 | 230 | 233 | 237 | 240 | 243 | 247 | 250 | 253 | 256 | 260
13 | 266 | 270 | 275 | 279 | 284 | 288 | 292 | 297 | 301 | 305
14 | 264 | 268 | 273 | 277 | 281 | 286 | 290 | 294 | 299 | 303
15 | 136 | 136 | 137 | 137 | 138 | 138 | 139 | 139 | 140 | 140
16 | 146 | 147 | 148 | 148 | 149 | 150 | 151 | 151 | 152 | 153
17 | 251 | 255 | 259 | 263 | 267 | 271 | 275 | 279 | 282 | 286
18 | 223 | 226 | 229 | 232 | 235 | 238 | 242 | 245 | 248 | 251
19 | 139 | 140 | 140 | 141 | 141 | 142 | 142 | 143 | 144 | 144
20 | 0 | 213 | 216 | 219 | 221 | 224 | 227 | 230 | 233 | 235
21 | 0 | 136 | 136 | 137 | 137 | 138 | 138 | 139 | 139 | 140
22 | 0 | 202 | 204 | 207 | 209 | 212 | 214 | 217 | 219 | 222
23 | 0 | 0 | 203 | 205 | 208 | 210 | 213 | 215 | 218 | 220
24 | 0 | 0 | 200 | 202 | 205 | 207 | 210 | 212 | 214 | 217
25 | 0 | 0 | 212 | 215 | 218 | 220 | 223 | 226 | 229 | 231
26 | 0 | 0 | 0 | 184 | 186 | 188 | 190 | 192 | 194 | 196
27 | 0 | 0 | 0 | 182 | 184 | 186 | 188 | 189 | 191 | 193
28 | 0 | 0 | 0 | 248 | 252 | 256 | 260 | 263 | 267 | 271
29 | 0 | 0 | 0 | 0 | 188 | 190 | 192 | 194 | 196 | 198
30 | 0 | 0 | 0 | 0 | 209 | 212 | 214 | 217 | 220 | 222
31 | 0 | 0 | 0 | 0 | 162 | 163 | 165 | 166 | 167 | 168
32 | 0 | 0 | 0 | 0 | 249 | 253 | 257 | 261 | 264 | 268
33 | 0 | 0 | 0 | 0 | 0 | 232 | 235 | 239 | 242 | 245
34 | 0 | 0 | 0 | 0 | 0 | 191 | 193 | 195 | 197 | 200
35 | 0 | 0 | 0 | 0 | 0 | 254 | 258 | 262 | 266 | 270
36 | 0 | 0 | 0 | 0 | 0 | 243 | 247 | 250 | 254 | 258
37 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 221 | 224 | 227
38 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 215 | 218 | 220
39 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 164 | 166 | 167
40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 221 | 224
41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 134 | 135
42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 246 | 249
43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 268 | 273
44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 273
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 216
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 228
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 138
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243

## Datos Líneas (hidden)
FROM | TO | LENGTH (km) | Resistencia |  |  | Impedancia |  |  | Conductors | Alternative 1 |  |  |  | Alternative 2
|  |  | Exist | 1 | 2 | Exist | 1 | 2 |  | Capacity (MVA) | Impedance (Ohmios/km) | Resistance (Ohmios/km) | C. Inver ($/km) | Capacity (MVA) | Impedance (Ohmios/km) | Resistance (Ohmios/km) | C. Inver ($/km)
201 | 1 | 0.83536 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0 | EFF & ERF | 6.28 | 0.557 |  | - | - | - |  | -
202 | 60 | 0.00472 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0 | NRF | 9 | 0.478 |  | 29870 | 12 | 0.423 |  | 39310
202 | 66 | 0.56169 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0 | NAF | 6.28 | 0.557 |  | 25030 | 9 | 0.478 |  | 34920
202 | 74 | 0.25014 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
202 | 95 | 0.39173 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0 | [7 empty] | VB | 13800
1 | 2 | 0.4106 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0 | [7 empty] | SB | 1000000
2 | 3 | 0.28789 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0 | [7 empty] | pf | 0.9
3 | 4 | 0.08019 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
4 | 5 | 0.58895 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
5 | 6 | 0.1537 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
6 | 7 | 0.44974 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
6 | 8 | 0.96991 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
8 | 9 | 0.16708 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
8 | 10 | 0.56753 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
10 | 11 | 0.08019 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
10 | 12 | 0.33196 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
10 | 13 | 0.83536 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
13 | 14 | 0.00472 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
13 | 15 | 0.56162 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
15 | 16 | 0.27374 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
20 | 21 | 0.80312 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
20 | 22 | 0.4578 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
22 | 23 | 0.34266 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
22 | 24 | 0.06135 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
24 | 25 | 0.11327 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
25 | 26 | 0.04719 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
26 | 27 | 0.16306 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
27 | 28 | 0.03341 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
28 | 29 | 0.21416 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
28 | 31 | 0.44974 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
29 | 30 | 0.08019 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
31 | 32 | 0.10708 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
32 | 33 | 0.47116 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
33 | 34 | 1.1285 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
36 | 37 | 0.10692 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
39 | 40 | 0.41762 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
39 | 46 | 0.29983 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
40 | 41 | 0.08015 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
41 | 42 | 0.83536 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
42 | 43 | 0.29733 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
42 | 51 | 3.1323 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
43 | 44 | 0.00472 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
43 | 52 | 0.17463 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
44 | 45 | 0.9209 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
46 | 47 | 0.16046 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
47 | 48 | 0.33037 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
48 | 49 | 0.15574 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
49 | 50 | 0.28789 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
52 | 53 | 1.401 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
53 | 54 | 0.40089 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
53 | 57 | 0.11327 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
54 | 55 | 0.06607 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
55 | 56 | 0.15102 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
57 | 58 | 0.07551 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
58 | 59 | 0.05191 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
60 | 61 | 0.27374 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
61 | 62 | 0.28912 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
62 | 63 | 0.47116 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
63 | 64 | 0.56753 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
64 | 65 | 0.37479 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
66 | 67 | 0.23558 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
67 | 68 | 0.34924 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
68 | 69 | 0.01887 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
69 | 70 | 1.6796 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
70 | 71 | 0.96279 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
71 | 72 | 0.83064 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
72 | 73 | 0.82592 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
74 | 75 | 0.42948 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
75 | 76 | 0.63178 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
76 | 77 | 0.14631 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
76 | 78 | 0.79241 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
78 | 79 | 1.1565 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
78 | 80 | 0.16991 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
80 | 81 | 1.3992 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
80 | 82 | 0.02831 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
82 | 83 | 1.8359 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
83 | 84 | 0.56634 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
84 | 85 | 0.52388 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
87 | 88 | 0.11799 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
90 | 91 | 0.87545 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
91 | 92 | 0.48117 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
92 | 93 | 0.64249 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
93 | 94 | 0.1537 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
95 | 96 | 0.64249 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
96 | 97 | 0.02831 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
97 | 98 | 1.0525 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
97 | 99 | 0.17214 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
99 | 100 | 1.1044 | 0.0026323 | 0 | 0 | 0.0029248 | 0 | 0
201 | 17 | 0.07949 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
201 | 35 | 0.19351 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
202 | 86 | 0.83536 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
17 | 18 | 0.21238 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
18 | 19 | 0.33509 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
19 | 20 | 0.41434 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
35 | 36 | 0.30741 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
36 | 38 | 0.37424 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
38 | 39 | 0.25958 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
86 | 87 | 0.33981 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
87 | 89 | 0.02359 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
89 | 90 | 0.42476 | 0.0026323 | 0.002259 | 0.0019991 | 0.0029248 | 0.00251 | 0.0022212
203 | 103 | 0.29733 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
203 | 108 | 2.4168 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
203 | 126 | 1.1469 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
203 | 130 | 1.751 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
11 | 121 | 1.1516 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
15 | 120 | 0.3328 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
15 | 121 | 0.35001 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
16 | 120 | 0.62108 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
30 | 113 | 0.61037 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
31 | 123 | 0.07459 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
45 | 108 | 0.53541 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
46 | 129 | 0.97444 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
50 | 101 | 0.64249 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
51 | 101 | 0.87807 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
56 | 107 | 1.2207 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
59 | 104 | 1.213 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
65 | 131 | 0.53541 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
65 | 133 | 0.81176 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
72 | 119 | 0.36812 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
85 | 111 | 0.3115 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
94 | 106 | 0.02831 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
94 | 110 | 1.633 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
100 | 128 | 0.11327 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
101 | 102 | 0.55651 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
102 | 103 | 1.0519 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
104 | 105 | 0.59966 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
105 | 122 | 0.24542 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
106 | 107 | 0.29733 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
107 | 122 | 0.34924 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
107 | 125 | 1.1085 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
108 | 109 | 0.23125 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
108 | 122 | 0.40588 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
109 | 110 | 0.53462 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
111 | 112 | 0.56136 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
112 | 113 | 0.41434 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
113 | 114 | 0.91656 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
114 | 123 | 1.7023 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
115 | 116 | 0.27626 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
115 | 129 | 0.90413 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
116 | 117 | 1.2549 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
117 | 118 | 0.86226 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
118 | 130 | 0.55548 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
119 | 120 | 0.64186 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
121 | 132 | 0.9643 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
123 | 124 | 0.58164 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
124 | 125 | 0.35712 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
126 | 127 | 1.3583 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
127 | 128 | 0.3593 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
132 | 133 | 0.30705 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
133 | 134 | 0.45277 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251
134 | 135 | 0.56097 | 0 | 0.0026323 | 0.002259 | 0 | 0.0029248 | 0.00251

## Datos Líneas 2 (hidden)
FROM | TO | LENGTH (km) | Resistencia |  |  | FROM | TO | Parámetro Aij linealizacion | [8 empty] | FROM | TO | Parámetro Bij linealizacion
|  |  | Exist | 1 | 2 |  |  | Exist.1 | Exist.2 | Exist.3 | 1.1 | 1.2 | 1.3 | 2.1 | 2.2 | 2.3 |  |  | Exist.1 | Exist.2 | Exist.3 | 1.1 | 1.2 | 1.3 | 2.1 | 2.2 | 2.3
201 | 1 | 0.83536 | 0.0026323 | 0 | 0 | 201 | 1 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 1 | 0.0054202 | 0.026234 | 0.086723 | 0 | 0 | 0 | 0 | 0 | 0
202 | 60 | 0.00472 | 0.0026323 | 0 | 0 | 202 | 60 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 60 | 3.0625e-05 | 0.00014823 | 0.00049001 | 0 | 0 | 0 | 0 | 0 | 0
202 | 66 | 0.56169 | 0.0026323 | 0 | 0 | 202 | 66 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 66 | 0.0036445 | 0.017639 | 0.058312 | 0 | 0 | 0 | 0 | 0 | 0
202 | 74 | 0.25014 | 0.0026323 | 0 | 0 | 202 | 74 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 74 | 0.001623 | 0.0078554 | 0.025968 | 0 | 0 | 0 | 0 | 0 | 0
202 | 95 | 0.39173 | 0.0026323 | 0 | 0 | 202 | 95 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 95 | 0.0025417 | 0.012302 | 0.040667 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | 0.4106 | 0.0026323 | 0 | 0 | 1 | 2 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0.0026641 | 0.012894 | 0.042626 | 0 | 0 | 0 | 0 | 0 | 0
2 | 3 | 0.28789 | 0.0026323 | 0 | 0 | 2 | 3 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0.001868 | 0.0090409 | 0.029887 | 0 | 0 | 0 | 0 | 0 | 0
3 | 4 | 0.08019 | 0.0026323 | 0 | 0 | 3 | 4 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0.00052031 | 0.0025183 | 0.0083249 | 0 | 0 | 0 | 0 | 0 | 0
4 | 5 | 0.58895 | 0.0026323 | 0 | 0 | 4 | 5 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0.0038214 | 0.018495 | 0.061142 | 0 | 0 | 0 | 0 | 0 | 0
5 | 6 | 0.1537 | 0.0026323 | 0 | 0 | 5 | 6 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0.00099727 | 0.0048268 | 0.015956 | 0 | 0 | 0 | 0 | 0 | 0
6 | 7 | 0.44974 | 0.0026323 | 0 | 0 | 6 | 7 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 7 | 0.0029181 | 0.014124 | 0.04669 | 0 | 0 | 0 | 0 | 0 | 0
6 | 8 | 0.96991 | 0.0026323 | 0 | 0 | 6 | 8 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 8 | 0.0062932 | 0.030459 | 0.10069 | 0 | 0 | 0 | 0 | 0 | 0
8 | 9 | 0.16708 | 0.0026323 | 0 | 0 | 8 | 9 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 9 | 0.0010841 | 0.005247 | 0.017345 | 0 | 0 | 0 | 0 | 0 | 0
8 | 10 | 0.56753 | 0.0026323 | 0 | 0 | 8 | 10 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 10 | 0.0036824 | 0.017823 | 0.058918 | 0 | 0 | 0 | 0 | 0 | 0
10 | 11 | 0.08019 | 0.0026323 | 0 | 0 | 10 | 11 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 0.00052031 | 0.0025183 | 0.0083249 | 0 | 0 | 0 | 0 | 0 | 0
10 | 12 | 0.33196 | 0.0026323 | 0 | 0 | 10 | 12 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 12 | 0.0021539 | 0.010425 | 0.034462 | 0 | 0 | 0 | 0 | 0 | 0
10 | 13 | 0.83536 | 0.0026323 | 0 | 0 | 10 | 13 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 13 | 0.0054202 | 0.026234 | 0.086723 | 0 | 0 | 0 | 0 | 0 | 0
13 | 14 | 0.00472 | 0.0026323 | 0 | 0 | 13 | 14 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 14 | 3.0625e-05 | 0.00014823 | 0.00049001 | 0 | 0 | 0 | 0 | 0 | 0
13 | 15 | 0.56162 | 0.0026323 | 0 | 0 | 13 | 15 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 15 | 0.003644 | 0.017637 | 0.058304 | 0 | 0 | 0 | 0 | 0 | 0
15 | 16 | 0.27374 | 0.0026323 | 0 | 0 | 15 | 16 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 0.0017761 | 0.0085965 | 0.028418 | 0 | 0 | 0 | 0 | 0 | 0
20 | 21 | 0.80312 | 0.0026323 | 0 | 0 | 20 | 21 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 21 | 0.005211 | 0.025221 | 0.083376 | 0 | 0 | 0 | 0 | 0 | 0
20 | 22 | 0.4578 | 0.0026323 | 0 | 0 | 20 | 22 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 22 | 0.0029704 | 0.014377 | 0.047526 | 0 | 0 | 0 | 0 | 0 | 0
22 | 23 | 0.34266 | 0.0026323 | 0 | 0 | 22 | 23 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 23 | 0.0022233 | 0.010761 | 0.035573 | 0 | 0 | 0 | 0 | 0 | 0
22 | 24 | 0.06135 | 0.0026323 | 0 | 0 | 22 | 24 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 24 | 0.00039806 | 0.0019266 | 0.006369 | 0 | 0 | 0 | 0 | 0 | 0
24 | 25 | 0.11327 | 0.0026323 | 0 | 0 | 24 | 25 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 25 | 0.00073494 | 0.0035571 | 0.011759 | 0 | 0 | 0 | 0 | 0 | 0
25 | 26 | 0.04719 | 0.0026323 | 0 | 0 | 25 | 26 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 0.00030619 | 0.001482 | 0.004899 | 0 | 0 | 0 | 0 | 0 | 0
26 | 27 | 0.16306 | 0.0026323 | 0 | 0 | 26 | 27 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 27 | 0.001058 | 0.0051207 | 0.016928 | 0 | 0 | 0 | 0 | 0 | 0
27 | 28 | 0.03341 | 0.0026323 | 0 | 0 | 27 | 28 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 28 | 0.00021678 | 0.0010492 | 0.0034684 | 0 | 0 | 0 | 0 | 0 | 0
28 | 29 | 0.21416 | 0.0026323 | 0 | 0 | 28 | 29 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 29 | 0.0013896 | 0.0067255 | 0.022233 | 0 | 0 | 0 | 0 | 0 | 0
28 | 31 | 0.44974 | 0.0026323 | 0 | 0 | 28 | 31 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 31 | 0.0029181 | 0.014124 | 0.04669 | 0 | 0 | 0 | 0 | 0 | 0
29 | 30 | 0.08019 | 0.0026323 | 0 | 0 | 29 | 30 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 30 | 0.00052031 | 0.0025183 | 0.0083249 | 0 | 0 | 0 | 0 | 0 | 0
31 | 32 | 0.10708 | 0.0026323 | 0 | 0 | 31 | 32 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 32 | 0.00069478 | 0.0033627 | 0.011116 | 0 | 0 | 0 | 0 | 0 | 0
32 | 33 | 0.47116 | 0.0026323 | 0 | 0 | 32 | 33 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 33 | 0.0030571 | 0.014796 | 0.048913 | 0 | 0 | 0 | 0 | 0 | 0
33 | 34 | 1.1285 | 0.0026323 | 0 | 0 | 33 | 34 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 34 | 0.0073221 | 0.035439 | 0.11715 | 0 | 0 | 0 | 0 | 0 | 0
36 | 37 | 0.10692 | 0.0026323 | 0 | 0 | 36 | 37 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 37 | 0.00069374 | 0.0033577 | 0.0111 | 0 | 0 | 0 | 0 | 0 | 0
39 | 40 | 0.41762 | 0.0026323 | 0 | 0 | 39 | 40 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 40 | 0.0027097 | 0.013115 | 0.043355 | 0 | 0 | 0 | 0 | 0 | 0
39 | 46 | 0.29983 | 0.0026323 | 0 | 0 | 39 | 46 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 46 | 0.0019454 | 0.0094158 | 0.031127 | 0 | 0 | 0 | 0 | 0 | 0
40 | 41 | 0.08015 | 0.0026323 | 0 | 0 | 40 | 41 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 41 | 0.00052005 | 0.002517 | 0.0083207 | 0 | 0 | 0 | 0 | 0 | 0
41 | 42 | 0.83536 | 0.0026323 | 0 | 0 | 41 | 42 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 41 | 42 | 0.0054202 | 0.026234 | 0.086723 | 0 | 0 | 0 | 0 | 0 | 0
42 | 43 | 0.29733 | 0.0026323 | 0 | 0 | 42 | 43 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 43 | 0.0019292 | 0.0093373 | 0.030867 | 0 | 0 | 0 | 0 | 0 | 0
42 | 51 | 3.1323 | 0.0026323 | 0 | 0 | 42 | 51 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 51 | 0.020324 | 0.098367 | 0.32518 | 0 | 0 | 0 | 0 | 0 | 0
43 | 44 | 0.00472 | 0.0026323 | 0 | 0 | 43 | 44 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 44 | 3.0625e-05 | 0.00014823 | 0.00049001 | 0 | 0 | 0 | 0 | 0 | 0
43 | 52 | 0.17463 | 0.0026323 | 0 | 0 | 43 | 52 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 52 | 0.0011331 | 0.0054841 | 0.018129 | 0 | 0 | 0 | 0 | 0 | 0
44 | 45 | 0.9209 | 0.0026323 | 0 | 0 | 44 | 45 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 45 | 0.0059752 | 0.02892 | 0.095603 | 0 | 0 | 0 | 0 | 0 | 0
46 | 47 | 0.16046 | 0.0026323 | 0 | 0 | 46 | 47 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 47 | 0.0010411 | 0.0050391 | 0.016658 | 0 | 0 | 0 | 0 | 0 | 0
47 | 48 | 0.33037 | 0.0026323 | 0 | 0 | 47 | 48 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 48 | 0.0021436 | 0.010375 | 0.034297 | 0 | 0 | 0 | 0 | 0 | 0
48 | 49 | 0.15574 | 0.0026323 | 0 | 0 | 48 | 49 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 49 | 0.0010105 | 0.0048909 | 0.016168 | 0 | 0 | 0 | 0 | 0 | 0
49 | 50 | 0.28789 | 0.0026323 | 0 | 0 | 49 | 50 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 50 | 0.001868 | 0.0090409 | 0.029887 | 0 | 0 | 0 | 0 | 0 | 0
52 | 53 | 1.401 | 0.0026323 | 0 | 0 | 52 | 53 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 53 | 0.0090901 | 0.043996 | 0.14544 | 0 | 0 | 0 | 0 | 0 | 0
53 | 54 | 0.40089 | 0.0026323 | 0 | 0 | 53 | 54 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 54 | 0.0026011 | 0.01259 | 0.041618 | 0 | 0 | 0 | 0 | 0 | 0
53 | 57 | 0.11327 | 0.0026323 | 0 | 0 | 53 | 57 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 57 | 0.00073494 | 0.0035571 | 0.011759 | 0 | 0 | 0 | 0 | 0 | 0
54 | 55 | 0.06607 | 0.0026323 | 0 | 0 | 54 | 55 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0.00042869 | 0.0020749 | 0.006859 | 0 | 0 | 0 | 0 | 0 | 0
55 | 56 | 0.15102 | 0.0026323 | 0 | 0 | 55 | 56 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 56 | 0.00097988 | 0.0047426 | 0.015678 | 0 | 0 | 0 | 0 | 0 | 0
57 | 58 | 0.07551 | 0.0026323 | 0 | 0 | 57 | 58 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 58 | 0.00048994 | 0.0023713 | 0.007839 | 0 | 0 | 0 | 0 | 0 | 0
58 | 59 | 0.05191 | 0.0026323 | 0 | 0 | 58 | 59 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 59 | 0.00033681 | 0.0016302 | 0.005389 | 0 | 0 | 0 | 0 | 0 | 0
60 | 61 | 0.27374 | 0.0026323 | 0 | 0 | 60 | 61 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 61 | 0.0017761 | 0.0085965 | 0.028418 | 0 | 0 | 0 | 0 | 0 | 0
61 | 62 | 0.28912 | 0.0026323 | 0 | 0 | 61 | 62 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 62 | 0.0018759 | 0.0090795 | 0.030015 | 0 | 0 | 0 | 0 | 0 | 0
62 | 63 | 0.47116 | 0.0026323 | 0 | 0 | 62 | 63 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 63 | 0.0030571 | 0.014796 | 0.048913 | 0 | 0 | 0 | 0 | 0 | 0
63 | 64 | 0.56753 | 0.0026323 | 0 | 0 | 63 | 64 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 64 | 0.0036824 | 0.017823 | 0.058918 | 0 | 0 | 0 | 0 | 0 | 0
64 | 65 | 0.37479 | 0.0026323 | 0 | 0 | 64 | 65 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 65 | 0.0024318 | 0.01177 | 0.038909 | 0 | 0 | 0 | 0 | 0 | 0
66 | 67 | 0.23558 | 0.0026323 | 0 | 0 | 66 | 67 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 67 | 0.0015285 | 0.0073981 | 0.024457 | 0 | 0 | 0 | 0 | 0 | 0
67 | 68 | 0.34924 | 0.0026323 | 0 | 0 | 67 | 68 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 68 | 0.002266 | 0.010968 | 0.036256 | 0 | 0 | 0 | 0 | 0 | 0
68 | 69 | 0.01887 | 0.0026323 | 0 | 0 | 68 | 69 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 69 | 0.00012244 | 0.00059259 | 0.001959 | 0 | 0 | 0 | 0 | 0 | 0
69 | 70 | 1.6796 | 0.0026323 | 0 | 0 | 69 | 70 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 70 | 0.010898 | 0.052747 | 0.17437 | 0 | 0 | 0 | 0 | 0 | 0
70 | 71 | 0.96279 | 0.0026323 | 0 | 0 | 70 | 71 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 71 | 0.006247 | 0.030235 | 0.099952 | 0 | 0 | 0 | 0 | 0 | 0
71 | 72 | 0.83064 | 0.0026323 | 0 | 0 | 71 | 72 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 72 | 0.0053895 | 0.026085 | 0.086233 | 0 | 0 | 0 | 0 | 0 | 0
72 | 73 | 0.82592 | 0.0026323 | 0 | 0 | 72 | 73 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 73 | 0.0053589 | 0.025937 | 0.085743 | 0 | 0 | 0 | 0 | 0 | 0
74 | 75 | 0.42948 | 0.0026323 | 0 | 0 | 74 | 75 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 75 | 0.0027866 | 0.013487 | 0.044586 | 0 | 0 | 0 | 0 | 0 | 0
75 | 76 | 0.63178 | 0.0026323 | 0 | 0 | 75 | 76 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 76 | 0.0040993 | 0.01984 | 0.065588 | 0 | 0 | 0 | 0 | 0 | 0
76 | 77 | 0.14631 | 0.0026323 | 0 | 0 | 76 | 77 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 77 | 0.00094932 | 0.0045947 | 0.015189 | 0 | 0 | 0 | 0 | 0 | 0
76 | 78 | 0.79241 | 0.0026323 | 0 | 0 | 76 | 78 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 78 | 0.0051415 | 0.024885 | 0.082264 | 0 | 0 | 0 | 0 | 0 | 0
78 | 79 | 1.1565 | 0.0026323 | 0 | 0 | 78 | 79 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 79 | 0.0075039 | 0.036319 | 0.12006 | 0 | 0 | 0 | 0 | 0 | 0
78 | 80 | 0.16991 | 0.0026323 | 0 | 0 | 78 | 80 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 80 | 0.0011024 | 0.0053358 | 0.017639 | 0 | 0 | 0 | 0 | 0 | 0
80 | 81 | 1.3992 | 0.0026323 | 0 | 0 | 80 | 81 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 81 | 0.0090786 | 0.04394 | 0.14526 | 0 | 0 | 0 | 0 | 0 | 0
80 | 82 | 0.02831 | 0.0026323 | 0 | 0 | 80 | 82 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 82 | 0.00018369 | 0.00088905 | 0.002939 | 0 | 0 | 0 | 0 | 0 | 0
82 | 83 | 1.8359 | 0.0026323 | 0 | 0 | 82 | 83 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 83 | 0.011912 | 0.057655 | 0.19059 | 0 | 0 | 0 | 0 | 0 | 0
83 | 84 | 0.56634 | 0.0026323 | 0 | 0 | 83 | 84 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 84 | 0.0036747 | 0.017785 | 0.058794 | 0 | 0 | 0 | 0 | 0 | 0
84 | 85 | 0.52388 | 0.0026323 | 0 | 0 | 84 | 85 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 85 | 0.0033992 | 0.016452 | 0.054386 | 0 | 0 | 0 | 0 | 0 | 0
87 | 88 | 0.11799 | 0.0026323 | 0 | 0 | 87 | 88 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 88 | 0.00076557 | 0.0037054 | 0.012249 | 0 | 0 | 0 | 0 | 0 | 0
90 | 91 | 0.87545 | 0.0026323 | 0 | 0 | 90 | 91 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 91 | 0.0056803 | 0.027493 | 0.090885 | 0 | 0 | 0 | 0 | 0 | 0
91 | 92 | 0.48117 | 0.0026323 | 0 | 0 | 91 | 92 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 92 | 0.003122 | 0.015111 | 0.049953 | 0 | 0 | 0 | 0 | 0 | 0
92 | 93 | 0.64249 | 0.0026323 | 0 | 0 | 92 | 93 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 93 | 0.0041687 | 0.020177 | 0.0667 | 0 | 0 | 0 | 0 | 0 | 0
93 | 94 | 0.1537 | 0.0026323 | 0 | 0 | 93 | 94 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 94 | 0.00099727 | 0.0048268 | 0.015956 | 0 | 0 | 0 | 0 | 0 | 0
95 | 96 | 0.64249 | 0.0026323 | 0 | 0 | 95 | 96 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 96 | 0.0041687 | 0.020177 | 0.0667 | 0 | 0 | 0 | 0 | 0 | 0
96 | 97 | 0.02831 | 0.0026323 | 0 | 0 | 96 | 97 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 97 | 0.00018369 | 0.00088905 | 0.002939 | 0 | 0 | 0 | 0 | 0 | 0
97 | 98 | 1.0525 | 0.0026323 | 0 | 0 | 97 | 98 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 98 | 0.0068291 | 0.033053 | 0.10926 | 0 | 0 | 0 | 0 | 0 | 0
97 | 99 | 0.17214 | 0.0026323 | 0 | 0 | 97 | 99 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 99 | 0.0011169 | 0.0054059 | 0.017871 | 0 | 0 | 0 | 0 | 0 | 0
99 | 100 | 1.1044 | 0.0026323 | 0 | 0 | 99 | 100 | 1.57 | 3.454 | 6.28 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 100 | 0.0071658 | 0.034683 | 0.11465 | 0 | 0 | 0 | 0 | 0 | 0
201 | 17 | 0.07949 | 0.0026323 | 0.002259 | 0.0019991 | 201 | 17 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 201 | 17 | 0.00051576 | 0.0024963 | 0.0082522 | 0.00090905 | 0.0043998 | 0.014545 | 0.0014301 | 0.0069219 | 0.022882
201 | 35 | 0.19351 | 0.0026323 | 0.002259 | 0.0019991 | 201 | 35 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 201 | 35 | 0.0012556 | 0.006077 | 0.020089 | 0.002213 | 0.010711 | 0.035408 | 0.0034815 | 0.016851 | 0.055705
202 | 86 | 0.83536 | 0.0026323 | 0.002259 | 0.0019991 | 202 | 86 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 202 | 86 | 0.0054202 | 0.026234 | 0.086723 | 0.0095532 | 0.046238 | 0.15285 | 0.015029 | 0.072742 | 0.24047
17 | 18 | 0.21238 | 0.0026323 | 0.002259 | 0.0019991 | 17 | 18 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 17 | 18 | 0.001378 | 0.0066696 | 0.022048 | 0.0024288 | 0.011755 | 0.038861 | 0.003821 | 0.018494 | 0.061137
18 | 19 | 0.33509 | 0.0026323 | 0.002259 | 0.0019991 | 18 | 19 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 18 | 19 | 0.0021742 | 0.010523 | 0.034787 | 0.0038321 | 0.018547 | 0.061314 | 0.0060288 | 0.029179 | 0.09646
19 | 20 | 0.41434 | 0.0026323 | 0.002259 | 0.0019991 | 19 | 20 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 19 | 20 | 0.0026884 | 0.013012 | 0.043015 | 0.0047384 | 0.022934 | 0.075815 | 0.0074546 | 0.03608 | 0.11927
35 | 36 | 0.30741 | 0.0026323 | 0.002259 | 0.0019991 | 35 | 36 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 35 | 36 | 0.0019946 | 0.0096539 | 0.031914 | 0.0035156 | 0.017015 | 0.056249 | 0.0055308 | 0.026769 | 0.088492
36 | 38 | 0.37424 | 0.0026323 | 0.002259 | 0.0019991 | 36 | 38 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 36 | 38 | 0.0024282 | 0.011753 | 0.038852 | 0.0042798 | 0.020714 | 0.068477 | 0.0067331 | 0.032588 | 0.10773
38 | 39 | 0.25958 | 0.0026323 | 0.002259 | 0.0019991 | 38 | 39 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 38 | 39 | 0.0016843 | 0.0081518 | 0.026948 | 0.0029686 | 0.014368 | 0.047497 | 0.0046702 | 0.022604 | 0.074724
86 | 87 | 0.33981 | 0.0026323 | 0.002259 | 0.0019991 | 86 | 87 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 86 | 87 | 0.0022048 | 0.010671 | 0.035277 | 0.0038861 | 0.018809 | 0.062178 | 0.0061137 | 0.02959 | 0.097819
87 | 89 | 0.02359 | 0.0026323 | 0.002259 | 0.0019991 | 87 | 89 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 87 | 89 | 0.00015306 | 0.00074082 | 0.002449 | 0.00026978 | 0.0013057 | 0.0043164 | 0.00042442 | 0.0020542 | 0.0067907
89 | 90 | 0.42476 | 0.0026323 | 0.002259 | 0.0019991 | 89 | 90 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 3 | 6.6 | 12 | 89 | 90 | 0.002756 | 0.013339 | 0.044096 | 0.0048576 | 0.023511 | 0.077721 | 0.0076421 | 0.036988 | 0.12227
203 | 103 | 0.29733 | 0 | 0.0026323 | 0.002259 | 203 | 103 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 203 | 103 | 0 | 0 | 0 | 0.0019292 | 0.0093373 | 0.030867 | 0.0034003 | 0.016457 | 0.054405
203 | 108 | 2.4168 | 0 | 0.0026323 | 0.002259 | 203 | 108 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 203 | 108 | 0 | 0 | 0 | 0.015681 | 0.075897 | 0.2509 | 0.027639 | 0.13377 | 0.44222
203 | 126 | 1.1469 | 0 | 0.0026323 | 0.002259 | 203 | 126 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 203 | 126 | 0 | 0 | 0 | 0.0074416 | 0.036017 | 0.11907 | 0.013116 | 0.063482 | 0.20986
203 | 130 | 1.751 | 0 | 0.0026323 | 0.002259 | 203 | 130 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 203 | 130 | 0 | 0 | 0 | 0.011361 | 0.054988 | 0.18178 | 0.020025 | 0.096919 | 0.32039
11 | 121 | 1.1516 | 0 | 0.0026323 | 0.002259 | 11 | 121 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 11 | 121 | 0 | 0 | 0 | 0.0074721 | 0.036165 | 0.11955 | 0.01317 | 0.063742 | 0.21072
15 | 120 | 0.3328 | 0 | 0.0026323 | 0.002259 | 15 | 120 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 15 | 120 | 0 | 0 | 0 | 0.0021593 | 0.010451 | 0.03455 | 0.0038059 | 0.018421 | 0.060895
15 | 121 | 0.35001 | 0 | 0.0026323 | 0.002259 | 15 | 121 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 15 | 121 | 0 | 0 | 0 | 0.002271 | 0.010992 | 0.036336 | 0.0040027 | 0.019373 | 0.064044
16 | 120 | 0.62108 | 0 | 0.0026323 | 0.002259 | 16 | 120 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 16 | 120 | 0 | 0 | 0 | 0.0040298 | 0.019504 | 0.064477 | 0.0071027 | 0.034377 | 0.11364
30 | 113 | 0.61037 | 0 | 0.0026323 | 0.002259 | 30 | 113 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 30 | 113 | 0 | 0 | 0 | 0.0039603 | 0.019168 | 0.063365 | 0.0069802 | 0.033784 | 0.11168
31 | 123 | 0.07459 | 0 | 0.0026323 | 0.002259 | 31 | 123 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 31 | 123 | 0 | 0 | 0 | 0.00048397 | 0.0023424 | 0.0077435 | 0.00085302 | 0.0041286 | 0.013648
45 | 108 | 0.53541 | 0 | 0.0026323 | 0.002259 | 45 | 108 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 45 | 108 | 0 | 0 | 0 | 0.003474 | 0.016814 | 0.055583 | 0.006123 | 0.029635 | 0.097968
46 | 129 | 0.97444 | 0 | 0.0026323 | 0.002259 | 46 | 129 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 46 | 129 | 0 | 0 | 0 | 0.0063226 | 0.030601 | 0.10116 | 0.011144 | 0.053936 | 0.1783
50 | 101 | 0.64249 | 0 | 0.0026323 | 0.002259 | 50 | 101 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 50 | 101 | 0 | 0 | 0 | 0.0041687 | 0.020177 | 0.0667 | 0.0073476 | 0.035562 | 0.11756
51 | 101 | 0.87807 | 0 | 0.0026323 | 0.002259 | 51 | 101 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 51 | 101 | 0 | 0 | 0 | 0.0056973 | 0.027575 | 0.091157 | 0.010042 | 0.048602 | 0.16067
56 | 107 | 1.2207 | 0 | 0.0026323 | 0.002259 | 56 | 107 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 56 | 107 | 0 | 0 | 0 | 0.0079204 | 0.038335 | 0.12673 | 0.01396 | 0.067567 | 0.22336
59 | 104 | 1.213 | 0 | 0.0026323 | 0.002259 | 59 | 104 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 59 | 104 | 0 | 0 | 0 | 0.0078705 | 0.038093 | 0.12593 | 0.013872 | 0.06714 | 0.22195
65 | 131 | 0.53541 | 0 | 0.0026323 | 0.002259 | 65 | 131 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 65 | 131 | 0 | 0 | 0 | 0.003474 | 0.016814 | 0.055583 | 0.006123 | 0.029635 | 0.097968
65 | 133 | 0.81176 | 0 | 0.0026323 | 0.002259 | 65 | 133 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 65 | 133 | 0 | 0 | 0 | 0.005267 | 0.025492 | 0.084273 | 0.0092834 | 0.044931 | 0.14853
72 | 119 | 0.36812 | 0 | 0.0026323 | 0.002259 | 72 | 119 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 72 | 119 | 0 | 0 | 0 | 0.0023885 | 0.01156 | 0.038216 | 0.0042099 | 0.020376 | 0.067358
85 | 111 | 0.3115 | 0 | 0.0026323 | 0.002259 | 85 | 111 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 85 | 111 | 0 | 0 | 0 | 0.0020211 | 0.0097823 | 0.032338 | 0.0035623 | 0.017242 | 0.056997
94 | 106 | 0.02831 | 0 | 0.0026323 | 0.002259 | 94 | 106 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 94 | 106 | 0 | 0 | 0 | 0.00018369 | 0.00088905 | 0.002939 | 0.00032376 | 0.001567 | 0.0051801
94 | 110 | 1.633 | 0 | 0.0026323 | 0.002259 | 94 | 110 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 94 | 110 | 0 | 0 | 0 | 0.010596 | 0.051283 | 0.16953 | 0.018675 | 0.090388 | 0.2988
100 | 128 | 0.11327 | 0 | 0.0026323 | 0.002259 | 100 | 128 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 100 | 128 | 0 | 0 | 0 | 0.00073494 | 0.0035571 | 0.011759 | 0.0012954 | 0.0062696 | 0.020726
101 | 102 | 0.55651 | 0 | 0.0026323 | 0.002259 | 101 | 102 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 101 | 102 | 0 | 0 | 0 | 0.0036109 | 0.017477 | 0.057774 | 0.0063643 | 0.030803 | 0.10183
102 | 103 | 1.0519 | 0 | 0.0026323 | 0.002259 | 102 | 103 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 102 | 103 | 0 | 0 | 0 | 0.0068252 | 0.033034 | 0.1092 | 0.01203 | 0.058224 | 0.19248
104 | 105 | 0.59966 | 0 | 0.0026323 | 0.002259 | 104 | 105 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 104 | 105 | 0 | 0 | 0 | 0.0038908 | 0.018832 | 0.062254 | 0.0068578 | 0.033192 | 0.10972
105 | 122 | 0.24542 | 0 | 0.0026323 | 0.002259 | 105 | 122 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 105 | 122 | 0 | 0 | 0 | 0.0015924 | 0.0077072 | 0.025478 | 0.0028066 | 0.013584 | 0.044906
106 | 107 | 0.29733 | 0 | 0.0026323 | 0.002259 | 106 | 107 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 106 | 107 | 0 | 0 | 0 | 0.0019292 | 0.0093373 | 0.030867 | 0.0034003 | 0.016457 | 0.054405
107 | 122 | 0.34924 | 0 | 0.0026323 | 0.002259 | 107 | 122 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 107 | 122 | 0 | 0 | 0 | 0.002266 | 0.010968 | 0.036256 | 0.0039939 | 0.019331 | 0.063903
107 | 125 | 1.1085 | 0 | 0.0026323 | 0.002259 | 107 | 125 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 107 | 125 | 0 | 0 | 0 | 0.0071927 | 0.034813 | 0.11508 | 0.012677 | 0.061359 | 0.20284
108 | 109 | 0.23125 | 0 | 0.0026323 | 0.002259 | 108 | 109 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 108 | 109 | 0 | 0 | 0 | 0.0015004 | 0.0072622 | 0.024007 | 0.0026446 | 0.0128 | 0.042314
108 | 122 | 0.40588 | 0 | 0.0026323 | 0.002259 | 108 | 122 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 108 | 122 | 0 | 0 | 0 | 0.0026335 | 0.012746 | 0.042136 | 0.0046417 | 0.022466 | 0.074267
109 | 110 | 0.53462 | 0 | 0.0026323 | 0.002259 | 109 | 110 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 109 | 110 | 0 | 0 | 0 | 0.0034688 | 0.016789 | 0.055501 | 0.006114 | 0.029592 | 0.097823
111 | 112 | 0.56136 | 0 | 0.0026323 | 0.002259 | 111 | 112 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 111 | 112 | 0 | 0 | 0 | 0.0036423 | 0.017629 | 0.058277 | 0.0064198 | 0.031072 | 0.10272
112 | 113 | 0.41434 | 0 | 0.0026323 | 0.002259 | 112 | 113 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 112 | 113 | 0 | 0 | 0 | 0.0026884 | 0.013012 | 0.043015 | 0.0047384 | 0.022934 | 0.075815
113 | 114 | 0.91656 | 0 | 0.0026323 | 0.002259 | 113 | 114 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 113 | 114 | 0 | 0 | 0 | 0.005947 | 0.028784 | 0.095153 | 0.010482 | 0.050732 | 0.16771
114 | 123 | 1.7023 | 0 | 0.0026323 | 0.002259 | 114 | 123 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 114 | 123 | 0 | 0 | 0 | 0.011045 | 0.053459 | 0.17673 | 0.019468 | 0.094224 | 0.31148
115 | 116 | 0.27626 | 0 | 0.0026323 | 0.002259 | 115 | 116 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 115 | 116 | 0 | 0 | 0 | 0.0017925 | 0.0086755 | 0.028679 | 0.0031593 | 0.015291 | 0.050548
115 | 129 | 0.90413 | 0 | 0.0026323 | 0.002259 | 115 | 129 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 115 | 129 | 0 | 0 | 0 | 0.0058664 | 0.028393 | 0.093862 | 0.01034 | 0.050044 | 0.16544
116 | 117 | 1.2549 | 0 | 0.0026323 | 0.002259 | 116 | 117 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 116 | 117 | 0 | 0 | 0 | 0.0081425 | 0.03941 | 0.13028 | 0.014351 | 0.069461 | 0.22962
117 | 118 | 0.86226 | 0 | 0.0026323 | 0.002259 | 117 | 118 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 117 | 118 | 0 | 0 | 0 | 0.0055947 | 0.027078 | 0.089516 | 0.0098609 | 0.047727 | 0.15777
118 | 130 | 0.55548 | 0 | 0.0026323 | 0.002259 | 118 | 130 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 118 | 130 | 0 | 0 | 0 | 0.0036042 | 0.017444 | 0.057667 | 0.0063525 | 0.030746 | 0.10164
119 | 120 | 0.64186 | 0 | 0.0026323 | 0.002259 | 119 | 120 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 119 | 120 | 0 | 0 | 0 | 0.0041646 | 0.020157 | 0.066634 | 0.0073403 | 0.035527 | 0.11745
121 | 132 | 0.9643 | 0 | 0.0026323 | 0.002259 | 121 | 132 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 121 | 132 | 0 | 0 | 0 | 0.0062568 | 0.030283 | 0.10011 | 0.011028 | 0.053375 | 0.17645
123 | 124 | 0.58164 | 0 | 0.0026323 | 0.002259 | 123 | 124 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 123 | 124 | 0 | 0 | 0 | 0.0037739 | 0.018266 | 0.060383 | 0.0066517 | 0.032194 | 0.10643
124 | 125 | 0.35712 | 0 | 0.0026323 | 0.002259 | 124 | 125 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 124 | 125 | 0 | 0 | 0 | 0.0023171 | 0.011215 | 0.037074 | 0.0040841 | 0.019767 | 0.065345
126 | 127 | 1.3583 | 0 | 0.0026323 | 0.002259 | 126 | 127 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 126 | 127 | 0 | 0 | 0 | 0.008813 | 0.042655 | 0.14101 | 0.015533 | 0.075181 | 0.24853
127 | 128 | 0.3593 | 0 | 0.0026323 | 0.002259 | 127 | 128 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 127 | 128 | 0 | 0 | 0 | 0.0023313 | 0.011283 | 0.0373 | 0.004109 | 0.019887 | 0.065743
132 | 133 | 0.30705 | 0 | 0.0026323 | 0.002259 | 132 | 133 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 132 | 133 | 0 | 0 | 0 | 0.0019923 | 0.0096426 | 0.031877 | 0.0035115 | 0.016996 | 0.056184
133 | 134 | 0.45277 | 0 | 0.0026323 | 0.002259 | 133 | 134 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 133 | 134 | 0 | 0 | 0 | 0.0029378 | 0.014219 | 0.047005 | 0.005178 | 0.025061 | 0.082847
134 | 135 | 0.56097 | 0 | 0.0026323 | 0.002259 | 134 | 135 | 0 | 0 | 0 | 1.57 | 3.454 | 6.28 | 2.25 | 4.95 | 9 | 134 | 135 | 0 | 0 | 0 | 0.0036398 | 0.017617 | 0.058236 | 0.0064152 | 0.03105 | 0.10264

## Viento (hidden)
Demanda ordenada(MW) | Velocidad de viento ordenadas (m/s) | B1 | 6.1305
7.2758 | 2.3 | B2 | 9.1021 | Zone | Load level
6.9633 | 5.5 | B3 | 10.0495 |  | 1 | 2 | 3
6.9591 | 4.6 |  |  | A | 8.53 | 9.12 | 10.04
6.9434 | 3.5 |  |  | B | 6.13 | 7.26 | 7.11
6.8901 | 7 |  |  | C | 4.13 | 5.1 | 5.56
6.8807 | 7.5
6.8807 | 4.5
6.8598 | 6.9
6.8598 | 4.5
6.8347 | 3.7
6.8075 | 6.9
6.8012 | 3.2
6.7918 | 8.8
6.7866 | 5.5
6.7761 | 10.3
6.772 | 2.7
6.7646 | 6
6.7615 | 2.7
6.7605 | 8.8
6.7552 | 4.4
6.7448 | 5.5
6.7437 | 5.5
6.7343 | 8.7
6.7207 | 5.2
6.7197 | 3.6
6.6977 | 4.7
6.6967 | 6.7
6.6862 | 3.2
6.6821 | 7.7
6.6674 | 11.6
6.6653 | 2.3
6.6653 | 2.8
6.6476 | 6.6
6.6444 | 2.8
6.635 | 5
6.6298 | 6.3
6.6089 | 2.5
6.6036 | 0
6.5984 | 6.4
6.5942 | 0
6.5932 | 7.4
6.5786 | 4.7
6.5775 | 6
6.5775 | 7.2
6.5733 | 8.6
6.5723 | 6.8
6.5723 | 0
6.5671 | 2.5
6.565 | 8.6
6.5629 | 2.7
6.5618 | 5
6.5577 | 6.7
6.5556 | 3
6.5514 | 6.9
6.5451 | 4
6.542 | 8.9
6.542 | 5.9
6.5367 | 9
6.5315 | 4
6.5305 | 0
6.5305 | 6.3
6.5305 | 0
6.5252 | 4.6
6.52 | 8.4
6.52 | 1.8
6.5148 | 7.5
6.5148 | 8.5
6.5148 | 8.5
6.5148 | 2.5
6.5096 | 4.2
6.5043 | 5.1
6.5033 | 5
6.4991 | 3.5
6.4939 | 4.5
6.4928 | 7
6.4897 | 4
6.4887 | 6.8
6.4876 | 2.3
6.4834 | 5.3
6.4782 | 3
6.4782 | 5
6.4772 | 4
6.474 | 2.3
6.473 | 4
6.4636 | 3.8
6.4594 | 5.9
6.4573 | 3
6.4521 | 2.6
6.4468 | 11
6.4443 | 4.9
6.4333 | 4.5
6.4301 | 6.5
6.4299 | 2
6.428 | 7.5
6.4218 | 5.6
6.4218 | 0
6.4207 | 3.5
6.4164 | 5.05
6.4159 | 7.5
6.4155 | 3.6
6.4144 | 12.6
6.405 | 0
6.404 | 4
6.404 | 6.7
6.4008 | 1.1
6.4008 | 4.5
6.3998 | 7.5
6.3972 | 2
6.3962 | 5.7
6.3956 | 8.6
6.3946 | 4.7
6.3876 | 5.7
6.3841 | 8.2
6.3789 | 3.5
6.3785 | 8
6.3737 | 0
6.3737 | 5.5
6.3737 | 7.2
6.3726 | 6.7
6.3643 | 6.4
6.3632 | 8.6
6.359 | 5
6.358 | 3.2
6.354 | 5
6.3538 | 4.9
6.3528 | 5.5
6.3517 | 8.9
6.3517 | 5.5
6.3486 | 3.2
6.3475 | 3.8
6.3475 | 3.5
6.3475 | 4.2
6.3444 | 7.2
6.3413 | 3.7
6.3381 | 3.9
6.3371 | 2.9
6.3329 | 3.7
6.3318 | 0
6.3266 | 6
6.3266 | 7.1
6.3235 | 6.3
6.3214 | 5.4
6.3208 | 8.5
6.3203 | 7.2
6.3162 | 7.5
6.312 | 6.5
6.3112 | 7.5
6.3068 | 6
6.3057 | 1.875
6.3057 | 4.5
6.3001 | 6.3
6.2953 | 2.5
6.29 | 3.2
6.29 | 6.6
6.2859 | 3.7
6.2806 | 5.5
6.2754 | 5.6
6.2708 | 5.2
6.2649 | 4.3
6.2649 | 4
6.2618 | 6.5
6.2482 | 6.9
6.2449 | 5.5
6.244 | 4.2
6.243 | 4.5
6.2388 | 5.2
6.2386 | 5.1
6.2378 | 4.5
6.2377 | 2
6.2336 | 3.7
6.2325 | 6
6.2325 | 5.9
6.2294 | 7.6
6.2273 | 4.6
6.2273 | 4.7
6.2252 | 10.5
6.2242 | 7
6.2231 | 9.1
6.2185 | 2
6.2169 | 8.6
6.2169 | 6
6.2146 | 5.7
6.2127 | 3.8
6.2116 | 5.7
6.2074 | 0
6.205 | 5.3
6.2022 | 5.3
6.197 | 4.6
6.1907 | 3.4
6.1907 | 4
6.1855 | 5.6
6.1813 | 2
6.1803 | 5.3
6.1714 | 4.2
6.1698 | 3.1
6.1698 | 5
6.1635 | 7
6.1622 | 7.5
6.1594 | 7
6.15 | 0
6.15 | 4.5
6.1489 | 14.5
6.1489 | 5.3
6.1489 | 4.4
6.1395 | 10.5
6.1368 | 5.2
6.129 | 4.2
6.128 | 5.9
6.128 | 2.5
6.128 | 2.5
6.126 | 12.9
6.1217 | 3.5
6.1186 | 0
6.1185 | 4.6
6.1175 | 3.3
6.1175 | 2.5
6.1175 | 4
6.1134 | 5.3
6.1089 | 1.5
6.1071 | 10.5
6.1071 | 4.1
6.1029 | 4.2
6.0974 | 4
6.0972 | 14
6.0906 | 2.5
6.081 | 5.9
6.0801 | 3.2
6.0791 | 4
6.0757 | 4.6
6.0757 | 2.5
6.0705 | 1
6.0663 | 7
6.0663 | 4.5
6.0653 | 5.4
6.0647 | 0
6.0642 | 4.3
6.0637 | 3.5
6.0559 | 5.2
6.0496 | 7.2
6.0444 | 4.7
6.0391 | 11
6.0339 | 5.5
6.0339 | 5.3
6.0287 | 9
6.0282 | 0
6.0276 | 6.2
6.0272 | 7.9
6.0182 | 9
6.0182 | 6
6.0182 | 1.7
6.0176 | 2.5
6.0167 | 0
6.0118 | 2.5
6.0088 | 5.5
6.008 | 2.5
6.008 | 2
6.0078 | 12
6.0078 | 7.5
6.0042 | 0
6.0026 | 5.5
6.0026 | 4.7
5.9973 | 6
5.9964 | 0
5.9936 | 3.5
5.9911 | 12
5.99 | 4.5
5.9888 | 1
5.9879 | 4.9
5.9875 | 0
5.9869 | 6.8
5.9849 | 0
5.984 | 3.5
5.9816 | 4
5.9816 | 6
5.9792 | 2.5
5.9722 | 10.5
5.9722 | 6.8
5.9691 | 3.5
5.966 | 2
5.9618 | 6.5
5.9607 | 4.5
5.96 | 9.3
5.96 | 2
5.9555 | 5
5.9555 | 7
5.9555 | 6
5.9555 | 4
5.9503 | 4.2
5.9451 | 1.4
5.9451 | 6.7
5.9446 | 6
5.944 | 2.3
5.9398 | 2.5
5.9346 | 5.5
5.934 | 7
5.9335 | 0
5.9335 | 0
5.9302 | 0
5.9225 | 0
5.9215 | 2.5
5.9168 | 0
5.9137 | 6
5.9127 | 4
5.9085 | 8.6
5.9032 | 3.5
5.9013 | 0
5.9004 | 2.5
5.8991 | 7.6
5.8975 | 4
5.8912 | 5.5
5.8876 | 10.5
5.8876 | 5.3
5.8823 | 4
5.8782 | 4.2
5.8754 | 7.4
5.8744 | 0
5.8687 | 0
5.8667 | 3.9
5.8658 | 4.8
5.8656 | 8
5.8591 | 1.4
5.8571 | 6.5
5.8562 | 5
5.8562 | 7.3
5.8552 | 0
5.8514 | 8.3
5.8485 | 1.4
5.848 | 7.5
5.8457 | 11.4
5.8447 | 7.7
5.8444 | 12.3
5.8437 | 7
5.8435 | 13
5.839 | 13.1
5.8389 | 4
5.8379 | 8
5.837 | 5.9
5.8353 | 3.4
5.835 | 1
5.8346 | 8.9
5.8341 | 2.5
5.8301 | 12.5
5.8301 | 10
5.829 | 4
5.8256 | 7
5.8248 | 5.7
5.8238 | 3.6
5.8238 | 7.5
5.8217 | 7.8
5.8216 | 1.4
5.8197 | 5.6
5.8187 | 3.5
5.8166 | 0
5.8158 | 2.5
5.811 | 1
5.8102 | 3.6
5.8092 | 1.1
5.8092 | 5.5
5.8091 | 1
5.8081 | 3
5.8076 | 8.8
5.8072 | 3.1
5.804 | 6.8
5.8014 | 7.9
5.7995 | 1
5.7976 | 0
5.7966 | 3.5
5.7956 | 5
5.7903 | 2.2
5.7894 | 1.7
5.7883 | 1.1
5.7883 | 4.2
5.7879 | 4.9
5.783 | 7.5
5.7822 | 3
5.7803 | 1
5.7788 | 7.5
5.7778 | 6
5.7778 | 9.9
5.7778 | 5.7
5.7774 | 4
5.7768 | 8.8
5.7726 | 5.7
5.7726 | 1
5.7726 | 1
5.7716 | 16.8
5.7705 | 9.1
5.7673 | 4.6
5.7673 | 8
5.7658 | 5.5
5.763 | 4
5.7626 | 9.5
5.7621 | 3.5
5.762 | 1.1
5.761 | 9.6
5.761 | 1
5.761 | 4.8
5.761 | 8
5.7591 | 2.85
5.7569 | 1.1
5.7569 | 5.3
5.7545 | 15
5.7543 | 0
5.7536 | 0
5.7524 | 5.3
5.7491 | 12.2
5.7482 | 14.2
5.7454 | 8
5.7437 | 8.6
5.7428 | 2
5.7423 | 4.2
5.7419 | 1
5.7418 | 6.5
5.7412 | 4
5.7401 | 8.4
5.7356 | 13.2
5.7341 | 14.7
5.7293 | 3.5
5.7275 | 11.1
5.7266 | 12.1
5.7257 | 1
5.7245 | 0
5.723 | 10.4
5.7213 | 12
5.7213 | 6
5.7197 | 2.5
5.7197 | 6.8
5.7182 | 6.7
5.7161 | 4.2
5.7159 | 5.5
5.7158 | 14.2
5.713 | 1
5.713 | 4.6
5.7122 | 13.2
5.7098 | 6
5.7088 | 0
5.7068 | 6.6
5.7059 | 1
5.705 | 11.8
5.7046 | 4.35
5.701 | 6
5.7004 | 6
5.6994 | 5.5
5.6994 | 5.6
5.6951 | 12.6
5.6942 | 5.5
5.6915 | 6
5.6915 | 16.8
5.6861 | 6
5.6837 | 10.7
5.6795 | 14
5.6785 | 6
5.6774 | 2.4
5.6765 | 2.5
5.6764 | 7
5.6726 | 0
5.6712 | 5.4
5.67 | 1
5.6691 | 7.6
5.667 | 5.4
5.6669 | 3.8
5.6669 | 5.5
5.6646 | 6.4
5.6637 | 11.5
5.6637 | 11.4
5.6628 | 6.1
5.6628 | 7
5.6621 | 1
5.6621 | 10.6
5.6592 | 7.9
5.6576 | 6
5.6576 | 4.4
5.6563 | 7.2
5.6563 | 0
5.6556 | 14
5.6555 | 3
5.6555 | 1.5
5.6524 | 1
5.6524 | 10.5
5.6476 | 3.2
5.6471 | 6.6
5.6457 | 1
5.6457 | 11
5.6438 | 1.8
5.6371 | 4
5.6367 | 4.3
5.6342 | 0.5
5.6332 | 1
5.6331 | 9.8
5.6265 | 1
5.6241 | 3.8
5.6187 | 7
5.6187 | 13.2
5.6179 | 4
5.6168 | 10.5
5.6158 | 9.7
5.6147 | 3.8
5.6142 | 12.3
5.614 | 5
5.614 | 0.5
5.6121 | 1
5.6095 | 4
5.6092 | 8.2
5.6092 | 8.7
5.6053 | 7
5.6025 | 4.5
5.6011 | 3.4
5.6007 | 10.8
5.6001 | 9.2
5.598 | 4.7
5.5971 | 6.4
5.5957 | 3.4
5.5948 | 1
5.5948 | 8.5
5.5896 | 3.2
5.5886 | 8
5.5854 | 8.8
5.5852 | 1
5.5852 | 1
5.5842 | 19.9
5.5834 | 8
5.5804 | 2.8
5.58 | 1
5.5792 | 4.5
5.5791 | 11
5.5785 | 1
5.5775 | 6.5
5.5755 | 1
5.5755 | 12.5
5.5688 | 0
5.5687 | 5.5
5.5679 | 2
5.5679 | 5.9
5.5665 | 1
5.5665 | 7.9
5.5647 | 2
5.5612 | 9.7
5.5602 | 12
5.5593 | 4.5
5.5573 | 3.9
5.5563 | 1
5.5563 | 16.2
5.5544 | 1
5.5521 | 10.7
5.5512 | 12.2
5.551 | 4
5.5496 | 2
5.5485 | 10
5.5478 | 6
5.5477 | 3
5.5431 | 10.8
5.5426 | 11
5.5413 | 8.4
5.5395 | 5
5.5386 | 12.1
5.5377 | 7
5.5341 | 9
5.5332 | 13.1
5.5332 | 6.6
5.5296 | 11
5.5296 | 13
5.5248 | 9
5.5227 | 4.6
5.5198 | 1.7
5.5189 | 3
5.5108 | 8.6
5.5108 | 8
5.5091 | 3
5.509 | 8.5
5.5018 | 1
5.5018 | 13.2
5.5016 | 2.5
5.4987 | 1
5.4987 | 1
5.4964 | 12.9
5.4955 | 3
5.4946 | 11.6
5.4945 | 9
5.4937 | 9.7
5.4929 | 2
5.4929 | 0
5.4928 | 1
5.4928 | 1
5.49 | 5.5
5.4872 | 5.8
5.4861 | 2.7
5.483 | 10.7
5.483 | 3.9
5.482 | 0
5.482 | 0
5.4795 | 3
5.4795 | 1
5.4795 | 1
5.4795 | 3
5.4793 | 9.7
5.4775 | 7.1
5.4757 | 9.2
5.4725 | 1.4
5.4723 | 2.5
5.4708 | 5
5.4699 | 3.3
5.4699 | 7.2
5.4676 | 1
5.4658 | 13.2
5.4652 | 6.5
5.4622 | 5.7
5.4577 | 9.8
5.4523 | 12.4
5.4497 | 0
5.4478 | 8
5.446 | 2
5.446 | 13.5
5.4442 | 12.8
5.4424 | 13.1
5.442 | 2.6
5.4388 | 6.8
5.4388 | 1
5.4388 | 0
5.4381 | 5.7
5.4372 | 1
5.437 | 6
5.4353 | 1
5.4314 | 1
5.429 | 2.9
5.428 | 0
5.4276 | 8.2
5.4266 | 0.5
5.4234 | 5.7
5.4228 | 7
5.4224 | 3.9
5.4224 | 6.8
5.4218 | 1.75
5.4217 | 14
5.4208 | 1
5.4208 | 9
5.4199 | 1
5.418 | 5.3
5.4172 | 10.8
5.4151 | 5
5.4132 | 6.5
5.4119 | 7
5.4118 | 8
5.41 | 10
5.4098 | 3.9
5.4073 | 13
5.4067 | 2.8
5.4055 | 0
5.4028 | 7.7
5.4007 | 8.5
5.3994 | 9.6
5.3983 | 7.7
5.3983 | 13.1
5.3978 | 7
5.3973 | 6.2
5.3949 | 1
5.3947 | 14
5.3938 | 10
5.393 | 17.5
5.3911 | 5.6
5.3893 | 11
5.3866 | 13
5.3857 | 4.7
5.3843 | 3.5
5.3834 | 1
5.3803 | 13
5.3786 | 5.9
5.3776 | 12
5.3776 | 7
5.3776 | 5.4
5.3758 | 6.8
5.3758 | 9.4
5.3738 | 3
5.3718 | 1
5.3714 | 2.9
5.3709 | 2.6
5.3687 | 7
5.3642 | 7.4
5.3628 | 6.7
5.3622 | 5.5
5.3603 | 0
5.3579 | 0
5.3545 | 7.3
5.3545 | 7.8
5.3543 | 8.7
5.3523 | 4.5
5.3488 | 3.5
5.3471 | 1.4
5.3449 | 2
5.344 | 6.7
5.3429 | 8
5.3429 | 6.2
5.3426 | 9.3
5.3419 | 8.1
5.3399 | 9
5.3363 | 10.3
5.3353 | 11.4
5.3315 | 0
5.3314 | 0
5.3309 | 6.8
5.3296 | 6.9
5.3293 | 10
5.3286 | 2
5.3286 | 5.6
5.3283 | 3.5
5.3276 | 1.5
5.3264 | 11
5.3262 | 11.4
5.3219 | 9.8
5.3219 | 4
5.3161 | 3.2
5.3157 | 7
5.3151 | 5.9
5.3147 | 8
5.3129 | 10
5.3113 | 4.5
5.3075 | 2.4
5.3074 | 7
5.3039 | 1
5.3011 | 3
5.3003 | 3.6
5.2948 | 0.1
5.2921 | 0.5
5.2921 | 0
5.2907 | 6
5.2904 | 12.8
5.2896 | 0
5.2896 | 3.7
5.2886 | 6.4
5.2877 | 1
5.2859 | 1
5.2859 | 6
5.2823 | 8.9
5.2802 | 2
5.2787 | 8
5.2777 | 0
5.2777 | 4.5
5.276 | 7
5.275 | 8
5.2719 | 2
5.2697 | 5.5
5.2635 | 7
5.2634 | 7
5.2603 | 7.6
5.2598 | 17.6
5.2594 | 1.3
5.2593 | 3
5.2593 | 8.5
5.2589 | 9.2
5.2589 | 6
5.2584 | 1
5.2582 | 5
5.2565 | 0
5.256 | 3
5.2546 | 2.2
5.2536 | 5
5.2535 | 13
5.2527 | 7.2
5.2517 | 12
5.2517 | 7
5.249 | 6.3
5.2488 | 6
5.2478 | 3.5
5.246 | 4.7
5.245 | 6.5
5.2436 | 0
5.2436 | 0
5.2431 | 6.5
5.2431 | 4.9
5.2421 | 4.2
5.2409 | 0
5.2409 | 0
5.24 | 6
5.2394 | 8.2
5.2387 | 7.8
5.2355 | 12.4
5.2344 | 4.3
5.2337 | 1
5.2247 | 7
5.2247 | 2
5.2238 | 15.6
5.2217 | 7
5.2211 | 0
5.2164 | 4.5
5.2133 | 5.8
5.2131 | 10
5.2123 | 1
5.2114 | 5.7
5.2112 | 11.2
5.2104 | 20.2
5.2068 | 1
5.205 | 0
5.205 | 8
5.205 | 9
5.2027 | 6.5
5.2018 | 3
5.2017 | 0
5.2008 | 6
5.1992 | 4.6
5.1966 | 4
5.196 | 5
5.196 | 7.2
5.1934 | 4
5.1924 | 6.2
5.1915 | 11.3
5.1872 | 6.1
5.1861 | 0
5.1861 | 7.2
5.1834 | 3.9
5.1812 | 4
5.1789 | 16.7
5.1768 | 0
5.1768 | 0
5.1744 | 6.1
5.17 | 3.2
5.169 | 0
5.169 | 7.9
5.169 | 7
5.1652 | 1
5.1652 | 0
5.1648 | 4.1
5.1645 | 11.9
5.1645 | 12.8
5.1623 | 1
5.1591 | 5
5.1591 | 5.5
5.1585 | 1.3
5.1575 | 0
5.1566 | 7.8
5.1564 | 9.7
5.1555 | 6.5
5.1548 | 4.2
5.1537 | 0
5.1537 | 1
5.1527 | 5.5
5.1527 | 3
5.1518 | 15.3
5.1516 | 4.5
5.151 | 0
5.1508 | 3
5.1501 | 11
5.1499 | 10
5.1485 | 3.2
5.1475 | 7.7
5.147 | 5.3
5.1447 | 9
5.1444 | 10.1
5.1443 | 3
5.1443 | 5
5.1438 | 13.2
5.1422 | 0
5.142 | 0
5.1412 | 0
5.1348 | 12.6
5.1338 | 0
5.1287 | 1.85
5.1285 | 12.4
5.1278 | 3
5.1276 | 12.3
5.1276 | 2
5.1276 | 3.2
5.1258 | 13.2
5.124 | 0
5.1239 | 8.1
5.1229 | 8
5.1195 | 11.1
5.1177 | 7
5.1141 | 4.8
5.114 | 4.7
5.114 | 4
5.1129 | 5
5.1124 | 3
5.1114 | 5.7
5.1108 | 7.4
5.1088 | 0
5.1087 | 9.6
5.1087 | 12.8
5.1078 | 9
5.1078 | 1
5.1067 | 1.4
5.106 | 10
5.1051 | 8.6
5.1043 | 4.5
5.1042 | 1
5.1028 | 7.2
5.1025 | 5.1
5.1024 | 4.4
5.1018 | 4
5.1015 | 9.5
5.1014 | 0
5.0997 | 8.2
5.0997 | 7
5.0993 | 8.2
5.0983 | 0
5.0979 | 4.5
5.0952 | 0
5.0932 | 4.8
5.0929 | 3.2
5.0927 | 2.5
5.092 | 0
5.092 | 7.2
5.0916 | 12.6
5.0912 | 2.2
5.0907 | 9.5
5.0898 | 6
5.0889 | 3
5.0889 | 17.2
5.088 | 4.3
5.0839 | 7.2
5.0835 | 10
5.0831 | 5
5.0817 | 0
5.0816 | 0
5.0816 | 7.2
5.0807 | 1.525
5.079 | 9.2
5.079 | 7.5
5.0787 | 5
5.0774 | 6
5.0772 | 6
5.0772 | 6.2
5.0764 | 4
5.0754 | 9
5.0739 | 3.4
5.0727 | 8.8
5.0718 | 2
5.0711 | 5.3
5.0711 | 15.4
5.0683 | 4
5.0669 | 0
5.0667 | 4.8
5.0659 | 1
5.0646 | 1
5.0643 | 1
5.0637 | 10
5.0617 | 7
5.061 | 9.5
5.0607 | 3.7
5.0576 | 7
5.0553 | 6.5
5.0548 | 9.6
5.0548 | 1
5.0547 | 2.7
5.0539 | 9
5.0521 | 0
5.0512 | 3.9
5.0504 | 2.8
5.0471 | 3.9
5.0471 | 6.8
5.047 | 0
5.0463 | 9.7
5.0439 | 5.4
5.0422 | 5.5
5.0395 | 10.4
5.0389 | 6.4
5.0386 | 11.4
5.0374 | 1
5.0374 | 0
5.0374 | 6
5.0355 | 9.9
5.0345 | 8.5
5.0341 | 9.5
5.0336 | 0
5.0335 | 2
5.0323 | 5
5.0323 | 5.8
5.0307 | 3.6
5.0305 | 3.7
5.0304 | 3.5
5.0278 | 1.525
5.0278 | 12.8
5.0278 | 13
5.0278 | 10
5.0251 | 5.5
5.0241 | 7.9
5.023 | 0
5.0225 | 5.2
5.022 | 0
5.0217 | 14.1
5.0206 | 10
5.0199 | 3
5.0189 | 5.6
5.0163 | 2
5.0147 | 5.4
5.0147 | 5.5
5.0144 | 7.3
5.0144 | 1.3
5.0136 | 2
5.0126 | 7.9
5.0126 | 11.7
5.0115 | 1.5
5.0111 | 4.9
5.0096 | 7.5
5.0096 | 5.5
5.0086 | 6.4
5.0071 | 0
5.0067 | 5.2
5.0067 | 8.6
5.0054 | 5
5.0042 | 5.2
5.0035 | 7.8
5.0026 | 6.5
5.0026 | 4.9
4.9981 | 8.6
4.998 | 6.1
4.998 | 4.5
4.9979 | 5.9
4.9961 | 7.2
4.9942 | 1.3
4.9939 | 8.7
4.9939 | 0
4.9938 | 6.2
4.9936 | 12
4.9909 | 10.1
4.9898 | 5.5
4.9898 | 6.9
4.9894 | 1.7
4.9891 | 1
4.9891 | 4.5
4.9879 | 2.2
4.9875 | 1
4.9866 | 5.3
4.9866 | 9
4.9864 | 4.5
4.9858 | 6.8
4.9846 | 8.5
4.9836 | 0
4.9828 | 9
4.9826 | 5
4.9817 | 2
4.9817 | 5
4.9801 | 6
4.9798 | 5
4.9798 | 6.4
4.9769 | 5.7
4.976 | 2
4.9735 | 5.2
4.9735 | 3.5
4.9708 | 3
4.9708 | 0.1
4.9678 | 9.4
4.9676 | 7.5
4.9676 | 5.7
4.9675 | 3.1
4.9653 | 5.8
4.9653 | 5.1
4.9653 | 3.7
4.9621 | 6.5
4.9603 | 9
4.9572 | 5.4
4.9531 | 11
4.953 | 5
4.953 | 7
4.953 | 9
4.9522 | 3.4
4.952 | 5.6
4.952 | 2
4.9513 | 5.9
4.9509 | 2
4.9505 | 6
4.9499 | 6
4.949 | 1
4.9481 | 5.8
4.9481 | 1.3
4.9468 | 13
4.9467 | 3
4.9441 | 8.1
4.9424 | 3.5
4.9408 | 3.8
4.9394 | 0.1
4.9394 | 7.4
4.936 | 4.6
4.9356 | 1
4.9346 | 7.5
4.9342 | 4
4.9326 | 3.5
4.9321 | 8.2
4.9315 | 0.5
4.9306 | 6.9
4.9298 | 1.4
4.9297 | 4.5
4.929 | 2.7
4.9288 | 1.5
4.9269 | 6.5
4.9269 | 11.9
4.9261 | 10.2
4.9261 | 2.7
4.9252 | 2
4.9203 | 6
4.9203 | 7
4.9189 | 7.5
4.918 | 9.9
4.9171 | 3.7
4.9162 | 6.7
4.9162 | 7.5
4.9154 | 13.6
4.9143 | 5.9
4.9122 | 1.4
4.9115 | 8.5
4.9113 | 4.1
4.9108 | 1
4.9081 | 2.9
4.9039 | 5.6
4.9038 | 6
4.901 | 2
4.8997 | 4.2
4.8983 | 6.5
4.8983 | 3.8
4.8976 | 11
4.8971 | 5.9
4.8914 | 1
4.8902 | 0
4.8892 | 5.9
4.888 | 7.8
4.8876 | 6
4.8875 | 6.5
4.8871 | 10.14
4.8866 | 0
4.8846 | 6.8
4.8835 | 8.3
4.883 | 9.2
4.883 | 5.9
4.8817 | 1.7
4.8803 | 8.4
4.8788 | 0
4.877 | 4.6
4.877 | 2.7
4.8769 | 2
4.8767 | 2.5
4.8745 | 2.7
4.874 | 7
4.8735 | 6.9
4.8735 | 5
4.8725 | 4.8
4.8721 | 7
4.8713 | 1.4
4.8704 | 3.2
4.8697 | 4.4
4.8688 | 3.6
4.8683 | 0
4.8672 | 4
4.8662 | 2.5
4.8641 | 4.6
4.8632 | 0
4.8632 | 8
4.8632 | 11.3
4.8623 | 10
4.8615 | 9.3
4.8615 | 9.7
4.8612 | 6
4.861 | 0
4.8596 | 6.2
4.859 | 1.4
4.859 | 7
4.8589 | 8
4.8587 | 4.9
4.8582 | 3.8
4.8579 | 3.7
4.8569 | 11.7
4.8558 | 6
4.8549 | 3.9
4.8542 | 0
4.8541 | 3.4
4.8508 | 5
4.8505 | 8.2
4.8505 | 0
4.8491 | 2
4.8479 | 6
4.8479 | 9
4.8476 | 4.7
4.8452 | 0
4.8452 | 0
4.8434 | 0
4.8404 | 0
4.8404 | 0
4.8389 | 1
4.8386 | 2.4
4.8377 | 4.8
4.8377 | 3.4
4.837 | 6.9
4.8349 | 7.9
4.8349 | 7.2
4.8345 | 1.9
4.8337 | 5
4.8337 | 9.6
4.8332 | 6.54
4.8326 | 10
4.8308 | 0
4.8307 | 1
4.8304 | 9
4.8304 | 5.5
4.8304 | 6.3
4.8287 | 9.4
4.8281 | 8.1
4.8279 | 3.9
4.8265 | 4.6
4.8263 | 13.2
4.8255 | 6.9
4.8255 | 4.4
4.8222 | 3
4.8209 | 1
4.8202 | 3.5
4.8202 | 0
4.8189 | 6
4.815 | 6.2
4.8146 | 8.9
4.814 | 2.5
4.814 | 2
4.8121 | 4.2
4.8108 | 4.5
4.8106 | 1
4.8099 | 6.2
4.8091 | 6.9
4.8091 | 2
4.8074 | 5.8
4.8068 | 7.4
4.8067 | 4
4.8058 | 5.2
4.8046 | 5.4
4.8046 | 8.3
4.8042 | 9.3
4.8035 | 10.8
4.8029 | 4.99
4.8011 | 5.8
4.8011 | 4.5
4.8004 | 2.5
4.8001 | 7
4.7983 | 9.4
4.7972 | 0
4.7943 | 10.6
4.7939 | 10
4.7931 | 0.1
4.793 | 1
4.793 | 7
4.7929 | 3.3
4.7905 | 2.5
4.7905 | 9.1
4.7903 | 5.9
4.7895 | 3.8
4.7889 | 5
4.7862 | 7.6
4.7854 | 2.4
4.7849 | 1
4.7847 | 0
4.7813 | 3.5
4.7789 | 10.3
4.7786 | 4.9
4.7741 | 4
4.7732 | 8
4.7705 | 5
4.7682 | 5.8
4.7682 | 9.05
4.7669 | 11.2
4.7664 | 1.3
4.7664 | 7.4
4.766 | 1
4.765 | 6.3
4.7642 | 6.8
4.764 | 4.1
4.7617 | 2.5
4.7617 | 0
4.7616 | 1
4.7601 | 4.8
4.7601 | 3.6
4.757 | 6.7
4.7565 | 11
4.7559 | 8.4
4.7552 | 8.1
4.7551 | 9.6
4.7549 | 9
4.7535 | 10
4.7534 | 0
4.7533 | 8.1
4.7527 | 5.7
4.7519 | 2.7
4.7519 | 11.4
4.7516 | 9.2
4.7494 | 5.5
4.7491 | 5.1
4.7489 | 6
4.7489 | 9.8
4.7486 | 5.2
4.7486 | 8.8
4.7472 | 6.6
4.7463 | 0
4.7453 | 6.5
4.7445 | 2.4
4.7445 | 2.1
4.7429 | 2
4.74 | 10.5
4.7391 | 1
4.7376 | 12.7
4.7373 | 4.9
4.7366 | 12.4
4.7366 | 8.5
4.7363 | 4.5
4.7363 | 5.5
4.7345 | 4.2
4.7338 | 8.5
4.7331 | 4.2
4.7323 | 3
4.7319 | 8.2
4.7314 | 2.8
4.7306 | 7.9
4.729 | 4.2
4.728 | 7
4.728 | 7.2
4.7251 | 1.85
4.7247 | 4.6
4.7241 | 0.7
4.722 | 5.1
4.722 | 6
4.7211 | 1
4.7175 | 7
4.7166 | 6
4.7165 | 6.1
4.7159 | 1.85
4.7159 | 0
4.7155 | 8
4.7147 | 2
4.7136 | 3.5
4.7118 | 4.4
4.711 | 5.7
4.7103 | 11
4.7088 | 5.5
4.7088 | 3.2
4.7085 | 7.1
4.7085 | 9.5
4.7085 | 7.1
4.7069 | 3.3
4.7063 | 11.4
4.704 | 1.5
4.7036 | 3.2
4.7028 | 4.2
4.7013 | 6.8
4.7011 | 2.3
4.7004 | 5
4.6995 | 0
4.6991 | 5.1
4.699 | 8.8
4.699 | 11.5
4.6953 | 8
4.6946 | 7.4
4.6924 | 9
4.6924 | 11.4
4.6878 | 8.5
4.6854 | 1.5
4.6833 | 10.7
4.6832 | 3
4.6788 | 12.2
4.678 | 6.5
4.6776 | 12.8
4.6758 | 6.6
4.6743 | 0
4.6713 | 1
4.6709 | 4.4
4.6709 | 4
4.6698 | 9
4.6697 | 6.3
4.6697 | 5.7
4.6689 | 13
4.6688 | 8.9
4.6687 | 3.5
4.6677 | 2
4.6668 | 13.6
4.6655 | 1.5
4.6645 | 0
4.6633 | 9.7
4.6619 | 4.4
4.6607 | 9.2
4.6607 | 9.7
4.6595 | 5.4
4.6592 | 5.5
4.659 | 6.4
4.6587 | 9
4.6578 | 5.6
4.6572 | 4
4.6569 | 1.5
4.6564 | 5
4.6562 | 13.1
4.6546 | 9
4.6546 | 5
4.6546 | 4
4.6519 | 4.3
4.6518 | 4.9
4.6511 | 1.5
4.6509 | 5.7
4.6505 | 0
4.6488 | 5.6
4.6482 | 0
4.6473 | 9.2
4.6437 | 3
4.6431 | 11
4.6412 | 22
4.6392 | 4
4.639 | 9
4.6362 | 2.7
4.6321 | 5.8
4.6302 | 0
4.6302 | 5.2
4.6293 | 0
4.6293 | 6
4.6268 | 11
4.6242 | 7.1
4.6227 | 9.3
4.6221 | 8
4.6219 | 7.1
4.6219 | 3
4.621 | 5.2
4.6186 | 3.6
4.6184 | 2
4.6178 | 5.5
4.6175 | 1.5
4.617 | 4.9
4.6167 | 9.5
4.6153 | 0.1
4.6153 | 2.9
4.6145 | 7.4
4.6106 | 10
4.6104 | 5.6
4.6104 | 6.7
4.6104 | 11
4.6096 | 6.7
4.6096 | 10
4.6088 | 6.1
4.6088 | 3.2
4.6086 | 11.4
4.607 | 5.2
4.6047 | 7.2
4.6031 | 14.5
4.6028 | 9.1
4.6024 | 10.1
4.6014 | 9.4
4.6014 | 13.9
4.6014 | 6
4.599 | 3.6
4.5989 | 6.5
4.5965 | 9.8
4.5965 | 7.2
4.596 | 10.1
4.5957 | 0
4.5954 | 6.1
4.5951 | 1
4.5946 | 8.6
4.5942 | 0
4.5935 | 4.8
4.5935 | 8.8
4.5933 | 7
4.5932 | 16
4.5915 | 6.3
4.5906 | 9.4
4.5903 | 6
4.5898 | 0
4.5898 | 4.4
4.5898 | 4.9
4.5886 | 1
4.5875 | 7.1
4.5875 | 4
4.5861 | 1
4.5844 | 8
4.584 | 0.1
4.5799 | 8.2
4.5795 | 21
4.5774 | 14.8
4.5772 | 1
4.5769 | 6
4.5769 | 2.5
4.5754 | 17
4.5749 | 7.8
4.5746 | 5.6
4.5742 | 5
4.5736 | 7.5
4.5702 | 10.4
4.5694 | 1.5
4.5694 | 1.5
4.5691 | 7
4.5687 | 7.8
4.5678 | 2.5
4.5666 | 12.1
4.5652 | 7
4.5652 | 4.5
4.5646 | 0
4.5646 | 1.5
4.5627 | 7
4.5611 | 11.7
4.5606 | 14.5
4.5592 | 5
4.5589 | 11.9
4.5574 | 5
4.5569 | 7.6
4.5559 | 6.2
4.5529 | 14.1
4.5523 | 5.7
4.5521 | 8.5
4.5511 | 9
4.5493 | 0
4.5491 | 0
4.5487 | 2
4.5483 | 9
4.543 | 12.2
4.5421 | 10
4.5411 | 3.2
4.5406 | 1.5
4.5402 | 13.7
4.5384 | 0
4.5368 | 9.1
4.536 | 6
4.5356 | 12
4.5344 | 8.9
4.5342 | 10
4.5328 | 3.4
4.5319 | 5.5
4.531 | 8.5
4.5286 | 2.8
4.5278 | 10.1
4.5272 | 5.6
4.527 | 13.6
4.5262 | 6.4
4.5247 | 2.6
4.5245 | 6.2
4.5232 | 7.8
4.5232 | 8.1
4.5218 | 10
4.5213 | 7
4.5205 | 2
4.5196 | 12.2
4.5185 | 5.5
4.5172 | 6.5
4.5171 | 1
4.5166 | 10.9
4.5162 | 10
4.5156 | 1.7
4.5156 | 0
4.5139 | 2
4.5129 | 6.2
4.5127 | 10.4
4.5118 | 5.1
4.5106 | 7.4
4.5102 | 25
4.5089 | 5.5
4.5077 | 6.7
4.5074 | 6
4.507 | 5.6
4.507 | 8.5
4.507 | 10.2
4.5052 | 11.9
4.5046 | 10.7
4.5022 | 13.8
4.5022 | 6.7
4.4993 | 5.3
4.4986 | 3.5
4.4984 | 8.6
4.4977 | 8
4.4962 | 11.1
4.4921 | 12.1
4.492 | 4
4.492 | 8.3
4.4918 | 7.1
4.4914 | 16.9
4.491 | 2
4.4902 | 4
4.4897 | 5.5
4.4877 | 5.5
4.4877 | 12.2
4.4869 | 6.3
4.4869 | 6
4.4857 | 6.7
4.4828 | 3
4.4826 | 8.5
4.4818 | 7.5
4.4781 | 2.5
4.4771 | 11.4
4.4763 | 3.7
4.4755 | 11.5
4.4747 | 5.3
4.4747 | 3.4
4.4747 | 5.5
4.4746 | 7
4.4746 | 6.4
4.4738 | 9.2
4.4733 | 7.2
4.4714 | 11
4.4709 | 6.8
4.4704 | 1
4.4704 | 7.2
4.4704 | 6
4.4701 | 6
4.4685 | 0.8
4.4685 | 11.5
4.4685 | 7.5
4.4674 | 14
4.4674 | 12
4.4665 | 7
4.4629 | 8
4.4608 | 9.5
4.4599 | 6
4.4589 | 10.7
4.4587 | 15
4.4573 | 20.4
4.4556 | 12.6
4.4548 | 12
4.4542 | 7
4.4541 | 6.5
4.4539 | 0.5
4.4533 | 4.5
4.4527 | 9.7
4.4519 | 1
4.4514 | 21.5
4.4502 | 5.8
4.4502 | 4.4
4.4494 | 10.6
4.4493 | 3.3
4.4485 | 0
4.4485 | 12
4.446 | 9.7
4.4458 | 9.5
4.4429 | 5.5
4.4416 | 7.2
4.4413 | 7
4.4412 | 20
4.4411 | 9.9
4.441 | 9.8
4.4404 | 2.3
4.4404 | 6.5
4.4404 | 6
4.4381 | 10.5
4.4379 | 1.5
4.4379 | 8.2
4.4377 | 6.9
4.4345 | 6.2
4.4311 | 10.3
4.4301 | 25
4.4297 | 2
4.4297 | 2
4.4291 | 2
4.4272 | 8.6
4.427 | 10.1
4.4253 | 7.9
4.4252 | 8
4.4243 | 9
4.424 | 5
4.4234 | 14
4.423 | 6.5
4.4225 | 11
4.4224 | 5.8
4.4224 | 2.4
4.4215 | 7.2
4.4207 | 7.6
4.4207 | 6.6
4.4202 | 4.7
4.4188 | 1.2
4.4176 | 8.5
4.4163 | 25
4.4153 | 9.4
4.4143 | 9
4.4135 | 9.8
4.4133 | 6.8
4.4126 | 14.9
4.4121 | 14
4.4121 | 10.5
4.4101 | 5.3
4.4099 | 3.4
4.4097 | 11.3
4.4092 | 17.6
4.4084 | 2
4.4084 | 7
4.4072 | 9
4.4061 | 8.6
4.4055 | 23.5
4.4054 | 4
4.4043 | 6.5
4.4043 | 10
4.404 | 11.1
4.4027 | 3
4.4013 | 4.7
4.4013 | 8.3
4.4011 | 3.6
4.4005 | 3.3
4.3995 | 15.8
4.3986 | 3
4.3986 | 3
4.3984 | 2
4.3983 | 6.9
4.3978 | 7.2
4.3973 | 10.2
4.3973 | 6.9
4.397 | 5.5
4.3955 | 0
4.3947 | 8.5
4.3945 | 8
4.3936 | 4.8
4.3916 | 4
4.3896 | 10.9
4.3883 | 11.8
4.3874 | 5
4.3872 | 8.4
4.3868 | 1
4.3864 | 28
4.3864 | 7.8
4.3855 | 8.2
4.3847 | 5.5
4.384 | 7
4.384 | 9.9
4.384 | 1
4.3826 | 10.7
4.3821 | 21.5
4.382 | 7.5
4.382 | 6
4.3814 | 8.35
4.3813 | 3
4.3812 | 7.9
4.3806 | 9
4.3804 | 4.7
4.3801 | 12
4.3793 | 8
4.3792 | 7.7
4.3792 | 8.5
4.3784 | 3.825
4.3775 | 7.5
4.3775 | 6
4.3772 | 2.5
4.377 | 4.1
4.3765 | 13.3
4.3753 | 5.1
4.3736 | 15
4.3733 | 2.7
4.373 | 14
4.3726 | 6.6
4.3724 | 8.2
4.3719 | 11.7
4.3712 | 6.4
4.3712 | 6
4.3712 | 2
4.3705 | 7.2
4.3704 | 2
4.37 | 7
4.3697 | 3.6
4.3697 | 13
4.369 | 10.5
4.3685 | 2
4.3685 | 12
4.3684 | 13.2
4.3684 | 2.5
4.3667 | 7.2
4.3646 | 25
4.3643 | 6.1
4.3638 | 2.2
4.3634 | 5.7
4.3604 | 4
4.3603 | 4.5
4.3602 | 5.5
4.3594 | 8
4.3573 | 14
4.3566 | 2
4.3561 | 4.2
4.3553 | 8.3
4.3551 | 7.9
4.3549 | 11.4
4.3532 | 9
4.3525 | 16.9
4.3523 | 6
4.352 | 3.7
4.3514 | 3.4
4.351 | 9.8
4.3508 | 9.6
4.3508 | 13.2
4.3504 | 8
4.3504 | 0
4.35 | 0
4.3493 | 8
4.3484 | 8.5
4.3479 | 5.2
4.3471 | 6
4.3456 | 6.1
4.3441 | 10.6
4.3438 | 3.9
4.3435 | 20
4.343 | 9.9
4.343 | 2.5
4.341 | 4
4.341 | 21.5
4.3406 | 10.4
4.3398 | 1
4.3381 | 9.5
4.3377 | 11.3
4.3374 | 14.7
4.3352 | 5
4.3348 | 11.6
4.3348 | 8
4.3348 | 2.9
4.3347 | 21
4.3347 | 9.9
4.334 | 9.8
4.3334 | 7.9
4.3331 | 8
4.3324 | 6.96
4.3316 | 6.2
4.3307 | 4.2
4.33 | 4.5
4.3292 | 2
4.3282 | 9.1
4.3282 | 12
4.3282 | 13.2
4.3275 | 7.5
4.3274 | 5.3
4.3267 | 7
4.326 | 13
4.325 | 9.2
4.3246 | 8
4.3246 | 10.85
4.3244 | 2.5
4.3244 | 7.8
4.3234 | 1.9
4.3231 | 7
4.3226 | 11.4
4.3226 | 4.5
4.3209 | 5.1
4.3196 | 3.5
4.3193 | 3.8
4.3193 | 13.4
4.3185 | 3.6
4.3183 | 1
4.3177 | 6.5
4.316 | 9.9
4.3158 | 11
4.3154 | 8.8
4.3145 | 0
4.3144 | 2.4
4.3144 | 11.2
4.3143 | 4.5
4.3137 | 8
4.3137 | 13
4.3129 | 2
4.3129 | 10
4.3128 | 2.6
4.3124 | 24.9
4.3122 | 3
4.3119 | 1
4.3118 | 5
4.3107 | 7.4
4.3103 | 6.5
4.31 | 10
4.3098 | 14.7
4.3093 | 2
4.308 | 8.5
4.3078 | 5.7
4.307 | 8.6
4.3064 | 11.9
4.3064 | 10.5
4.3059 | 9.5
4.3055 | 0
4.3055 | 15
4.3046 | 3
4.3045 | 6.5
4.3037 | 9.9
4.3035 | 7
4.3032 | 9
4.3029 | 0
4.3029 | 9.05
4.3004 | 5.3
4.3004 | 6.5
4.2998 | 6
4.2997 | 10
4.2984 | 9
4.298 | 11.8
4.2975 | 4.2
4.2965 | 0
4.2965 | 10
4.2963 | 16.6
4.2956 | 7.3
4.2948 | 6
4.2948 | 10.75
4.2947 | 5
4.2947 | 2.025
4.2936 | 7.5
4.292 | 15
4.2918 | 6
4.2914 | 15
4.2903 | 6
4.2899 | 6.1
4.2893 | 9.2
4.2893 | 10.4
4.2893 | 13.8
4.2889 | 7.6
4.2881 | 6.1
4.288 | 12.7
4.2879 | 3
4.2875 | 10
4.2865 | 16.5
4.2859 | 8
4.2857 | 5
4.2856 | 11
4.2848 | 13
4.2845 | 11.6
4.2841 | 20.5
4.2838 | 2
4.2833 | 7.7
4.2811 | 6.5
4.2811 | 8.5
4.2809 | 11.8
4.2801 | 8.9
4.2792 | 0
4.2783 | 5.5
4.278 | 8
4.2777 | 3
4.2777 | 7
4.2763 | 7.7
4.2761 | 14.6
4.276 | 5
4.2756 | 7.2
4.2743 | 9.6
4.2741 | 9.2
4.2739 | 11.3
4.2736 | 9.5
4.2735 | 4.2
4.273 | 3.3
4.271 | 10.8
4.2709 | 5
4.2708 | 10
4.2694 | 15.4
4.2693 | 2
4.2686 | 6.5
4.268 | 12.5
4.2677 | 6.5
4.2672 | 6.6
4.2672 | 5.3
4.267 | 4
4.2668 | 6.5
4.2665 | 12.4
4.2662 | 8
4.2661 | 3
4.2658 | 10.6
4.2653 | 4.2
4.264 | 9
4.2638 | 2.1
4.2633 | 9
4.2622 | 4
4.2621 | 9.4
4.262 | 7
4.2613 | 14.3
4.2613 | 14.9
4.2613 | 8
4.2612 | 3.4
4.2608 | 11.9
4.2597 | 7.3
4.2594 | 20.3
4.2591 | 10.6
4.2571 | 7.4
4.2565 | 4
4.2563 | 9.7
4.2562 | 6.5
4.2555 | 3
4.2554 | 13.2
4.2547 | 5.5
4.2543 | 8.8
4.2539 | 9.3
4.2536 | 14.3
4.2534 | 12.5
4.2523 | 3.5
4.2523 | 2.5
4.2522 | 12.4
4.2521 | 18.1
4.2516 | 7.5
4.2515 | 4.1
4.2511 | 23
4.2507 | 4.2
4.2503 | 12.3
4.2498 | 5.4
4.2494 | 1.1
4.2492 | 6.4
4.249 | 3.2
4.2489 | 1
4.2479 | 7.1
4.2475 | 1.4
4.2472 | 22
4.2465 | 14.3
4.2457 | 8
4.2453 | 12.2
4.2452 | 12.5
4.2452 | 0
4.2446 | 1
4.2427 | 7.35
4.2422 | 4.5
4.2416 | 6
4.2416 | 1
4.2416 | 8
4.2409 | 2
4.2408 | 22
4.2407 | 8.6
4.2401 | 22
4.239 | 8.6
4.2383 | 0
4.2383 | 1
4.2379 | 3.6
4.2372 | 14
4.2369 | 10.3
4.2367 | 8.7
4.2365 | 21
4.2365 | 6
4.2357 | 14.1
4.2342 | 3.7
4.2342 | 3.9
4.2338 | 14.5
4.2336 | 0
4.2336 | 2
4.2336 | 9.3
4.2336 | 0.7
4.233 | 6.5
4.2324 | 12.7
4.2307 | 7
4.2306 | 4
4.2306 | 5
4.2302 | 1
4.2302 | 5
4.2293 | 3
4.2293 | 7
4.2292 | 1
4.2286 | 3.7
4.2285 | 12.2
4.2278 | 5.6
4.2264 | 2
4.2264 | 9.5
4.2264 | 2.5
4.2263 | 13
4.2255 | 8
4.2254 | 5.3
4.2254 | 7.7
4.2244 | 4.7
4.2244 | 4.9
4.2236 | 14.3
4.2235 | 2.5
4.223 | 5.4
4.2228 | 16.4
4.2223 | 6
4.2221 | 12.9
4.2216 | 17.8
4.2214 | 0
4.2202 | 5
4.2201 | 5.8
4.2201 | 4.9
4.2194 | 1.4
4.2191 | 3.5
4.2181 | 6
4.2179 | 5.5
4.2162 | 13
4.2157 | 7.2
4.2155 | 7.5
4.215 | 7
4.215 | 7.4
4.213 | 3.3
4.2129 | 5.5
4.2125 | 6
4.2121 | 7.9
4.211 | 6.5
4.2102 | 2
4.2097 | 5
4.2097 | 6.1
4.2089 | 2.8
4.2085 | 10
4.2084 | 0.5
4.2081 | 4.5
4.2079 | 4
4.2059 | 11.3
4.2054 | 6.5
4.2052 | 7
4.2049 | 22
4.2048 | 1.4
4.2045 | 12.5
4.204 | 6.5
4.2038 | 8
4.2038 | 8
4.2035 | 3.5
4.203 | 6.6
4.2026 | 14.6
4.2024 | 3
4.2014 | 20
4.2008 | 16
4.2008 | 11.7
4.2006 | 12.8
4.1995 | 7.35
4.1994 | 8.5
4.1994 | 11.8
4.1993 | 5
4.1979 | 1
4.1976 | 18
4.1971 | 8.5
4.1967 | 6.7
4.1966 | 7.8
4.1958 | 4.4
4.1953 | 10.6
4.1943 | 18.5
4.1942 | 10
4.1936 | 15
4.1918 | 0.8
4.1906 | 8.9
4.1903 | 12.5
4.1899 | 2.8
4.1898 | 1.3
4.1898 | 7
4.1898 | 2.5
4.1895 | 7.2
4.1895 | 10.8
4.1894 | 13.2
4.1892 | 12
4.1888 | 5.4
4.1887 | 22
4.1886 | 10.9
4.1886 | 10
4.1873 | 3
4.1863 | 12
4.1863 | 15
4.1863 | 11.9
4.1859 | 16.5
4.1856 | 22
4.1855 | 9.2
4.1852 | 6.5
4.1845 | 10
4.1837 | 15.5
4.1827 | 28
4.1827 | 9
4.1825 | 7.9
4.1825 | 13.5
4.1819 | 10.85
4.1815 | 3.7
4.1812 | 8.5
4.1805 | 4
4.1803 | 4
4.1803 | 3
4.1803 | 5.5
4.1796 | 11.3
4.1795 | 3.7
4.1786 | 12.2
4.1784 | 5.2
4.1782 | 7.5
4.1775 | 21
4.1773 | 15.2
4.1769 | 2.5
4.1764 | 7.6
4.1763 | 8.5
4.1754 | 8.5
4.1754 | 7
4.1754 | 1
4.1754 | 12
4.1749 | 12.5
4.1746 | 19
4.1746 | 12.5
4.1745 | 13
4.1742 | 10.5
4.1742 | 8.3
4.1731 | 4.2
4.1731 | 9.5
4.1731 | 9.2
4.1728 | 4
4.1721 | 12
4.1721 | 5
4.172 | 11.6
4.1718 | 15.5
4.1713 | 9
4.1711 | 9.5
4.1711 | 4.9
4.1703 | 11.5
4.1703 | 11.3
4.1703 | 11.4
4.1703 | 3
4.1697 | 2
4.1696 | 7
4.1692 | 11
4.1691 | 2
4.1688 | 5.8
4.1681 | 22
4.1681 | 7
4.1674 | 1
4.1668 | 2
4.1666 | 1
4.1658 | 3.7
4.1647 | 10.3
4.1645 | 12
4.1645 | 12
4.1637 | 9.5
4.1629 | 4
4.1627 | 8.4
4.1627 | 10
4.162 | 15
4.162 | 15.2
4.1619 | 30
4.1616 | 5.4
4.1616 | 10.5
4.1615 | 8.2
4.1612 | 17.2
4.1612 | 12.5
4.161 | 8
4.1608 | 1
4.1607 | 5.8
4.1604 | 7.5
4.1604 | 3.3
4.1601 | 10
4.1591 | 5
4.159 | 12
4.158 | 0
4.1575 | 6.1
4.1572 | 15
4.1568 | 13.3
4.1562 | 19.2
4.1557 | 18
4.1556 | 8.1
4.1548 | 11.3
4.1548 | 11
4.1548 | 0.7
4.1535 | 11
4.1535 | 2.8
4.1535 | 13
4.1535 | 4
4.1533 | 3.8
4.1528 | 2
4.1526 | 6.8
4.1526 | 10.8
4.1517 | 11
4.1517 | 3
4.1503 | 17
4.1501 | 8
4.1499 | 10.8
4.1499 | 1
4.1493 | 10.5
4.149 | 4
4.1485 | 2
4.1482 | 18
4.1473 | 20.4
4.147 | 1
4.147 | 6
4.1468 | 10.3
4.1463 | 13
4.1463 | 2
4.1463 | 7.8
4.1459 | 8
4.1458 | 7
4.1455 | 8
4.1452 | 5
4.1447 | 2
4.1441 | 11.2
4.1436 | 0
4.1433 | 6.6
4.1433 | 2.8
4.1419 | 12.6
4.1407 | 5.1
4.1401 | 8.5
4.14 | 10.1
4.1397 | 9
4.1395 | 22.3
4.1394 | 3.6
4.1394 | 7.7
4.1393 | 13.7
4.139 | 2.8
4.139 | 9.6
4.1372 | 14.6
4.1369 | 7.9
4.1366 | 5.5
4.1366 | 2.8
4.1366 | 3.5
4.1361 | 10.5
4.1353 | 11.5
4.1353 | 3
4.1346 | 9.2
4.1345 | 10
4.134 | 8
4.1333 | 2
4.1333 | 7.5
4.1331 | 11.3
4.1328 | 4.9
4.1328 | 11
4.1322 | 8.3
4.1321 | 4.4
4.1313 | 6.1
4.1312 | 3
4.1312 | 7
4.131 | 6
4.1306 | 4.5
4.1303 | 6.7
4.1303 | 3.5
4.1292 | 4
4.1274 | 14
4.1274 | 3
4.1262 | 10.4
4.1262 | 4.6
4.1261 | 7.6
4.1259 | 8.1
4.1255 | 10
4.1255 | 8.8
4.1255 | 4.9
4.1254 | 15.2
4.1253 | 6.4
4.1248 | 4.5
4.1248 | 6.6
4.1244 | 9
4.1237 | 14.5
4.1236 | 10.5
4.1235 | 10.3
4.1233 | 18
4.123 | 2
4.1226 | 8
4.1226 | 7
4.1226 | 11.4
4.1226 | 17.4
4.1226 | 2.9
4.1218 | 2
4.1213 | 5.5
4.1212 | 10.5
4.1212 | 1
4.1209 | 9.8
4.1209 | 8.5
4.1208 | 9
4.1208 | 5.7
4.119 | 5.5
4.1188 | 12
4.1182 | 1
4.1182 | 5.9
4.1182 | 13.9
4.1182 | 5.5
4.1181 | 5.4
4.1164 | 15.5
4.1164 | 23
4.1164 | 8
4.1161 | 13.7
4.1156 | 5.7
4.113 | 1
4.113 | 12.4
4.1128 | 9.3
4.1118 | 0.7
4.1118 | 7
4.1113 | 25
4.111 | 1.5
4.111 | 16.8
4.111 | 5.5
4.1104 | 19.2
4.11 | 10
4.1099 | 6.4
4.1095 | 24.5
4.1095 | 1
4.1092 | 8.9
4.1091 | 2
4.1091 | 12.5
4.1075 | 4
4.107 | 12
4.107 | 2
4.1066 | 5.3
4.1062 | 12
4.1062 | 1
4.1052 | 6.2
4.1052 | 6
4.1047 | 9.8
4.1047 | 0.7
4.1047 | 7
4.1047 | 9
4.1037 | 16.8
4.1037 | 9.5
4.1026 | 8
4.1026 | 7
4.1025 | 2
4.1015 | 8
4.1008 | 6
4.1004 | 8.2
4.1001 | 12
4.0991 | 2
4.0986 | 16.2
4.0982 | 9
4.0982 | 10
4.0977 | 4.5
4.0972 | 8.6
4.0972 | 29
4.0968 | 5.5
4.0964 | 29
4.096 | 1
4.0958 | 19
4.0957 | 8.8
4.0957 | 4.3
4.0953 | 10
4.0953 | 11.5
4.095 | 19
4.0947 | 6
4.0946 | 12
4.0946 | 7.8
4.0945 | 7
4.0939 | 9.2
4.0939 | 14.8
4.0936 | 8.5
4.093 | 16
4.0917 | 15
4.0909 | 0
4.0909 | 12
4.0909 | 9.4
4.0903 | 8.4
4.0903 | 22
4.0903 | 17
4.0896 | 13.5
4.0893 | 16.5
4.0891 | 2
4.0891 | 12
4.0891 | 9
4.0888 | 9.2
4.0888 | 11.7
4.088 | 12
4.0868 | 19
4.0868 | 11
4.0855 | 18.6
4.0854 | 10
4.0851 | 2
4.0849 | 12.4
4.0849 | 7.5
4.0843 | 3.5
4.0843 | 5.6
4.0839 | 14
4.0833 | 21
4.0832 | 9.8
4.0832 | 12
4.0832 | 13.5
4.0819 | 11
4.0815 | 1
4.0814 | 15
4.0814 | 2
4.0808 | 12
4.0801 | 9.8
4.08 | 2
4.0793 | 1
4.0789 | 17
4.0789 | 5
4.0778 | 6.5
4.0773 | 5.5
4.0771 | 9.7
4.0768 | 12
4.0767 | 9.6
4.0764 | 11
4.0764 | 9.5
4.0761 | 10
4.076 | 8.8
4.076 | 12.2
4.0747 | 10.6
4.0746 | 2
4.0746 | 14.3
4.0746 | 12.5
4.0735 | 11.3
4.0735 | 8.7
4.0733 | 2.5
4.0732 | 7
4.0731 | 14.6
4.0728 | 7
4.0726 | 12.1
4.0724 | 12.9
4.0724 | 8
4.0721 | 5.6
4.0719 | 17.6
4.0717 | 9
4.0717 | 12.8
4.0715 | 5.4
4.0712 | 11
4.071 | 8
4.0698 | 14
4.0698 | 11.5
4.0697 | 2.5
4.0697 | 4.3
4.0697 | 9
4.0696 | 10
4.0689 | 16
4.0689 | 8.8
4.0689 | 13.5
4.0686 | 9.4
4.0684 | 16.7
4.0681 | 5.9
4.0677 | 5.6
4.0676 | 6.2
4.0676 | 3.4
4.0673 | 10.6
4.0663 | 8
4.0662 | 2.8
4.066 | 9
4.0658 | 8.1
4.0656 | 11.4
4.0647 | 13
4.0642 | 9.7
4.064 | 7
4.0638 | 10
4.0635 | 11.8
4.0634 | 3
4.0634 | 4.5
4.0633 | 5.9
4.0633 | 8.8
4.0633 | 8.1
4.0627 | 5.4
4.0626 | 11
4.062 | 13.8
4.062 | 22
4.062 | 7.9
4.062 | 7.8
4.0617 | 14.8
4.0617 | 17
4.0617 | 7.5
4.0617 | 5.1
4.0614 | 10.3
4.0609 | 9.4
4.06 | 10.5
4.0593 | 8.7
4.0592 | 15.5
4.0587 | 2
4.0582 | 6.7
4.0581 | 11.1
4.0576 | 6.6
4.0571 | 4
4.0564 | 8
4.0564 | 6.7
4.0561 | 7
4.0561 | 7.9
4.056 | 8.2
4.0553 | 2
4.055 | 18
4.0546 | 9.5
4.0546 | 6
4.0546 | 4.1
4.0545 | 12.3
4.0545 | 4
4.0534 | 9
4.0531 | 14.3
4.0527 | 4
4.0527 | 3.9
4.0524 | 7.9
4.0519 | 9.4
4.0519 | 11.4
4.0516 | 15
4.0516 | 12
4.0515 | 11.5
4.0515 | 7.5
4.051 | 13.4
4.051 | 8.6
4.051 | 7.8
4.0509 | 9.5
4.0508 | 3.4
4.0508 | 16
4.0502 | 20.3
4.0502 | 13.5
4.0502 | 14.5
4.05 | 8
4.048 | 11.2
4.0477 | 5
4.0474 | 19.1
4.0474 | 9.9
4.0473 | 11
4.047 | 3
4.047 | 25
4.047 | 23
4.047 | 5
4.0467 | 4.1
4.0466 | 16.6
4.0465 | 2
4.0463 | 14
4.0451 | 15
4.0445 | 7.2
4.0445 | 12.4
4.0444 | 14
4.044 | 10
4.0438 | 7.1
4.0438 | 9.7
4.0438 | 19
4.0438 | 19.6
4.0435 | 9.7
4.0431 | 3.5
4.0429 | 5
4.0425 | 11.2
4.0425 | 2.2
4.0425 | 5.9
4.0425 | 5
4.0424 | 9
4.0419 | 6
4.0419 | 4.7
4.0418 | 8.5
4.0416 | 12
4.0415 | 13.2
4.0414 | 4.4
4.0411 | 11.5
4.0409 | 8.7
4.0406 | 8.2
4.0405 | 4.5
4.0404 | 2
4.0404 | 7.8
4.0404 | 3.5
4.0404 | 3
4.0402 | 7.5
4.0395 | 21.2
4.0385 | 21
4.0382 | 9
4.0382 | 8.2
4.0373 | 12.9
4.0373 | 18
4.0368 | 18
4.0366 | 7.8
4.0364 | 9
4.0363 | 3.4
4.0362 | 4.3
4.0361 | 7.4
4.0359 | 16
4.0353 | 10
4.0352 | 11
4.0344 | 10.3
4.0342 | 10.1
4.0342 | 0
4.0342 | 2
4.0339 | 7
4.0335 | 15
4.0335 | 8.5
4.0332 | 7.5
4.0331 | 7.7
4.0331 | 8
4.033 | 2
4.0326 | 10.5
4.0324 | 24
4.0323 | 3.5
4.032 | 9.2
4.032 | 5
4.032 | 4
4.0317 | 9
4.0306 | 0
4.0302 | 7
4.0302 | 22
4.0299 | 8.6
4.0297 | 11
4.0295 | 7.2
4.0295 | 11.6
4.0295 | 8
4.0295 | 7.6
4.0294 | 12.8
4.0293 | 10
4.0291 | 2
4.0285 | 3.8
4.0285 | 13
4.0284 | 6.5
4.0284 | 11.5
4.028 | 9.5
4.0268 | 3.4
4.0268 | 4.5
4.0267 | 13.7
4.0265 | 5
4.0262 | 8.8
4.026 | 4.9
4.0259 | 2
4.0257 | 8
4.0255 | 7.9
4.0251 | 14
4.024 | 24
4.024 | 15
4.024 | 12
4.0237 | 6
4.0233 | 13
4.023 | 8.5
4.023 | 9.8
4.023 | 8.6
4.0226 | 21.2
4.0226 | 9.7
4.0226 | 1
4.0226 | 12
4.0223 | 13.9
4.0223 | 4.5
4.0219 | 8.8
4.0218 | 2
4.0216 | 4
4.0216 | 8.3
4.0216 | 3.5
4.0198 | 21.8
4.0198 | 9.5
4.0196 | 0
4.0192 | 2
4.0189 | 11.2
4.0188 | 1.5
4.0188 | 1.3
4.0187 | 8.6
4.0187 | 9.3
4.0187 | 2
4.0187 | 3.2
4.018 | 25
4.018 | 9.3
4.0169 | 10
4.0167 | 7.5
4.0164 | 8.5
4.0164 | 5
4.0163 | 10
4.0163 | 6.9
4.0163 | 6.2
4.0159 | 8.3
4.0159 | 3.7
4.0157 | 6
4.0157 | 7.1
4.0156 | 5.2
4.0146 | 6.3
4.0144 | 12.8
4.0143 | 5.2
4.0142 | 2.5
4.0138 | 9.1
4.0128 | 5
4.0128 | 2.3
4.0124 | 7.2
4.0124 | 5.8
4.0123 | 5.5
4.0116 | 12.1
4.0111 | 4.8
4.011 | 0
4.011 | 10
4.011 | 15
4.0109 | 12.5
4.0106 | 13.7
4.0105 | 5.8
4.01 | 4
4.0099 | 3.5
4.0098 | 7.4
4.0094 | 3.5
4.0093 | 12
4.0089 | 7
4.0089 | 7.1
4.0087 | 11.4
4.0087 | 7.8
4.0087 | 24
4.0086 | 19
4.0086 | 11
4.0084 | 6.2
4.008 | 0
4.0077 | 5.6
4.0075 | 6
4.0075 | 11
4.0073 | 3.7
4.0072 | 21.4
4.0072 | 10.5
4.0065 | 4
4.0063 | 4
4.0059 | 6.1
4.0059 | 5.4
4.0057 | 3.5
4.0057 | 10
4.0057 | 8.5
4.0051 | 13.5
4.0051 | 2
4.0048 | 9.2
4.0048 | 10.4
4.0048 | 12
4.0044 | 5.9
4.0044 | 8.3
4.0044 | 13.2
4.0044 | 6.5
4.0044 | 11
4.0044 | 1
4.0043 | 1
4.0043 | 0
4.0035 | 7.1
4.003 | 12.3
4.0025 | 7.2
4.0021 | 6.9
4.0021 | 3.4
4.0019 | 8
4.0014 | 9.2
4.0014 | 8
4.0012 | 13
4.0011 | 16
4.0008 | 13.6
4.0007 | 7
4.0007 | 7.4
4.0007 | 6
4.0007 | 6.5
3.9996 | 12.4
3.9996 | 1.3
3.9996 | 6
3.9996 | 5.3
3.9993 | 5
3.9987 | 12.6
3.9986 | 9
3.9986 | 4.5
3.9983 | 2
3.9981 | 1
3.9976 | 7.5
3.9976 | 11.9
3.9974 | 18
3.9973 | 2
3.9972 | 8.6
3.9971 | 9.8
3.9971 | 1
3.9971 | 10.8
3.9969 | 16
3.9968 | 9.5
3.9955 | 5.6
3.9947 | 12
3.9946 | 9.6
3.9945 | 10
3.9944 | 5.3
3.9942 | 12.6
3.9938 | 4.5
3.9938 | 21
3.9938 | 4.4
3.9934 | 14
3.9931 | 16.5
3.9927 | 8.3
3.9927 | 20.5
3.9925 | 8.4
3.9922 | 6.6
3.9917 | 8.4
3.9914 | 21.1
3.9913 | 10.6
3.9907 | 2
3.9904 | 7
3.9902 | 11.5
3.9901 | 11.3
3.9898 | 0
3.9898 | 10.4
3.989 | 2.2
3.9889 | 4
3.9888 | 5
3.9885 | 3
3.9878 | 5.1
3.9877 | 8.1
3.9875 | 22
3.9875 | 11
3.9873 | 17
3.9873 | 15
3.9873 | 6.7
3.9872 | 15.6
3.9871 | 4.7
3.9871 | 3.4
3.9867 | 13
3.9867 | 8
3.9865 | 19.4
3.9865 | 8.5
3.9864 | 10.5
3.9854 | 2
3.9853 | 14
3.9849 | 15.2
3.9849 | 0
3.9844 | 7.8
3.9837 | 5
3.9837 | 0
3.9836 | 15.2
3.9832 | 6.9
3.9832 | 10
3.9829 | 8.1
3.9829 | 23.5
3.9826 | 7.3
3.9825 | 9.8
3.9818 | 2
3.981 | 16.6
3.9808 | 5.6
3.9806 | 20
3.9802 | 4.5
3.9802 | 14
3.98 | 7
3.98 | 4.7
3.98 | 4
3.98 | 11.5
3.98 | 20.9
3.9799 | 3
3.9798 | 4.8
3.9793 | 26
3.9789 | 0
3.9789 | 18
3.9787 | 7.7
3.9786 | 9.9
3.9783 | 5.5
3.9783 | 16.2
3.9783 | 14.5
3.9781 | 3.6
3.9777 | 5.7
3.9776 | 8.2
3.9769 | 18.8
3.9767 | 6
3.976 | 6.2
3.9757 | 2
3.9757 | 10.1
3.9757 | 8.5
3.9757 | 17.9
3.9755 | 2.3
3.9755 | 2
3.9751 | 5.2
3.975 | 7
3.975 | 6.6
3.9747 | 10
3.9747 | 8.25
3.9745 | 1
3.9745 | 0
3.9741 | 9
3.9741 | 9
3.9738 | 10.6
3.9732 | 6
3.973 | 4
3.9728 | 27
3.9727 | 9.5
3.9723 | 9.8
3.9723 | 11
3.9713 | 5.5
3.9713 | 5.5
3.9709 | 10.3
3.9706 | 2.5
3.9703 | 11.2
3.9699 | 4.8
3.9693 | 6.9
3.9693 | 6
3.9693 | 4
3.9693 | 5.6
3.9687 | 9
3.9687 | 2.8
3.9686 | 8.5
3.9686 | 11.3
3.9686 | 22
3.9672 | 12.5
3.9671 | 8
3.9671 | 3
3.9671 | 6.3
3.967 | 2.5
3.9669 | 11
3.9663 | 17
3.9657 | 30
3.9657 | 5.9
3.9653 | 3.5
3.9652 | 5
3.9651 | 3.6
3.965 | 6.1
3.965 | 7.5
3.9644 | 6.5
3.9643 | 7.5
3.9641 | 7.4
3.9641 | 4.8
3.9638 | 7
3.9636 | 6.4
3.9635 | 21.3
3.9631 | 9
3.9628 | 6.3
3.9627 | 17
3.9625 | 14
3.9621 | 5.5
3.9621 | 17
3.9621 | 5
3.962 | 12
3.9617 | 6.2
3.9614 | 7
3.961 | 3.4
3.9607 | 11.9
3.9604 | 20
3.9603 | 5.5
3.9603 | 5.8
3.9597 | 7
3.9596 | 11.9
3.9595 | 7.5
3.9593 | 5.4
3.9588 | 5
3.9588 | 4
3.9588 | 7.8
3.9588 | 7.2
3.9587 | 4.3
3.9586 | 9.2
3.9586 | 0.1
3.9582 | 5.4
3.9575 | 5.1
3.9575 | 1
3.957 | 0
3.9568 | 8.1
3.9567 | 20.5
3.9565 | 5.4
3.9563 | 9.5
3.9563 | 12.9
3.9558 | 11.6
3.9556 | 12.2
3.9555 | 3.3
3.9555 | 1
3.9554 | 3
3.9554 | 4.8
3.9547 | 11.1
3.9547 | 9.1
3.9546 | 2.5
3.9536 | 6
3.9535 | 8.1
3.9534 | 9.8
3.9528 | 11.4
3.9528 | 21
3.9528 | 5
3.9527 | 14
3.9527 | 12
3.9526 | 15
3.9522 | 8.1
3.9517 | 3.8
3.9516 | 8
3.9513 | 9
3.9509 | 10.6
3.9509 | 8
3.9507 | 8.2
3.9505 | 2
3.9505 | 10.4
3.9505 | 9.7
3.9503 | 7.5
3.9498 | 0
3.9498 | 18.4
3.9495 | 10
3.9494 | 6.8
3.9494 | 7
3.9494 | 15
3.9487 | 30.5
3.9487 | 18.6
3.9484 | 7.8
3.9484 | 3.55
3.9484 | 3.5
3.948 | 18.3
3.9473 | 8.1
3.9473 | 7
3.9473 | 4
3.9471 | 5.5
3.9471 | 7.2
3.9469 | 11.5
3.9468 | 6.2
3.9466 | 8
3.9466 | 7.3
3.9466 | 16
3.9464 | 8.5
3.9461 | 5
3.9459 | 4.5
3.9456 | 6.2
3.9454 | 14.8
3.9453 | 6
3.9452 | 11
3.9448 | 5.2
3.9437 | 4.5
3.9437 | 1
3.9429 | 11.5
3.9424 | 15
3.9424 | 11.3
3.9424 | 8.5
3.9422 | 10.1
3.9422 | 13.4
3.9422 | 6.9
3.9421 | 14.3
3.9417 | 2
3.9417 | 11.5
3.9411 | 4.5
3.9411 | 5.5
3.941 | 9
3.9407 | 7.5
3.9407 | 10
3.9405 | 5.7
3.94 | 6.3
3.9399 | 8.1
3.9399 | 19.3
3.9398 | 7.5
3.9391 | 15
3.939 | 1
3.9382 | 5.1
3.9381 | 9.7
3.9379 | 6.5
3.9379 | 5.9
3.9378 | 11
3.9377 | 7.1
3.9375 | 11.2
3.9371 | 8.9
3.9371 | 6.8
3.9367 | 5.8
3.9361 | 17.4
3.9358 | 6
3.9357 | 13
3.935 | 11.5
3.9348 | 3.5
3.9347 | 5.5
3.9345 | 7
3.9345 | 9.8
3.9341 | 9.8
3.934 | 21
3.9334 | 6.8
3.9327 | 5.3
3.9326 | 4.7
3.9326 | 16
3.9314 | 12
3.9313 | 3.5
3.9309 | 7.3
3.9309 | 4.7
3.9308 | 0
3.9304 | 1
3.9301 | 7
3.9301 | 9
3.9301 | 7
3.9292 | 8
3.9279 | 9.5
3.9276 | 17
3.9276 | 18
3.9276 | 9.4
3.9275 | 5.8
3.9274 | 4
3.9273 | 5.5
3.9266 | 2
3.9266 | 10.2
3.9261 | 3
3.926 | 8
3.9256 | 10.5
3.9256 | 2
3.9256 | 12
3.9255 | 6
3.9254 | 13
3.925 | 2
3.9247 | 10.4
3.9243 | 1
3.9243 | 1
3.924 | 22
3.9233 | 21
3.9228 | 6
3.9228 | 3.5
3.9223 | 5.4
3.9221 | 20.3
3.922 | 13.9
3.9218 | 11.5
3.9213 | 12.5
3.9208 | 7.6
3.9208 | 6.3
3.9206 | 8.9
3.9206 | 5.1
3.9202 | 4.5
3.9202 | 5
3.9202 | 11.5
3.9199 | 6.5
3.9196 | 17
3.9195 | 10.6
3.9195 | 21
3.9188 | 10.8
3.9185 | 6.5
3.9181 | 12
3.9178 | 0.7
3.9178 | 12
3.9178 | 9.5
3.9177 | 13.5
3.9177 | 9
3.917 | 7.6
3.917 | 9.7
3.9167 | 4.7
3.9167 | 8.9
3.916 | 6
3.9156 | 14.8
3.9151 | 4.7
3.9151 | 5.5
3.915 | 9
3.9149 | 3.2
3.9146 | 20
3.9145 | 3.5
3.9143 | 11
3.9136 | 9.6
3.9134 | 9.8
3.9131 | 6.3
3.9125 | 10
3.9117 | 9.5
3.9116 | 9.5
3.9113 | 8.9
3.9112 | 1
3.9104 | 6.4
3.91 | 12
3.9099 | 7
3.9096 | 5.9
3.9096 | 5.4
3.9093 | 7.5
3.9091 | 10.8
3.909 | 12
3.9089 | 6
3.9083 | 4
3.9077 | 10
3.9073 | 10.5
3.9073 | 0
3.9072 | 2
3.9072 | 4.5
3.9072 | 11
3.9072 | 7.3
3.9069 | 2
3.9068 | 1
3.9068 | 8.8
3.9066 | 6.4
3.9066 | 5
3.9066 | 3.4
3.9066 | 4
3.9066 | 3.5
3.9065 | 21
3.9064 | 20
3.9064 | 9.4
3.9045 | 11
3.9045 | 6.7
3.9044 | 2.7
3.9038 | 13.7
3.9036 | 5
3.9036 | 10.7
3.9034 | 6
3.9031 | 6.4
3.903 | 17
3.903 | 14
3.9024 | 17
3.9018 | 16.4
3.9016 | 9.3
3.9016 | 5.2
3.9016 | 9.1
3.9013 | 14.8
3.9013 | 15.6
3.9013 | 10
3.9002 | 5
3.9002 | 12.5
3.9002 | 6.7
3.8999 | 8
3.8998 | 9.7
3.8998 | 9.3
3.8998 | 8
3.8995 | 8
3.8995 | 9.5
3.8995 | 12.6
3.8993 | 6.2
3.8986 | 7
3.8984 | 5.6
3.8982 | 5.23
3.8981 | 9.7
3.8978 | 11
3.8977 | 13.9
3.8973 | 14.5
3.8971 | 9.5
3.8971 | 6.6
3.897 | 8
3.8966 | 12
3.8966 | 5.8
3.8964 | 10
3.8964 | 4.7
3.8964 | 5
3.8961 | 7.5
3.896 | 21.7
3.896 | 21.4
3.896 | 3.3
3.8953 | 7.8
3.8953 | 3
3.8953 | 7.5
3.8953 | 11
3.8952 | 2
3.8949 | 3.5
3.8948 | 4.3
3.8945 | 8.9
3.8941 | 14.6
3.8939 | 3.1
3.8939 | 13
3.8934 | 7
3.8933 | 4.4
3.8931 | 11.5
3.8927 | 6.5
3.8924 | 15
3.8924 | 16
3.8921 | 6.7
3.8919 | 1.4
3.8916 | 7.6
3.8914 | 2
3.8914 | 12.9
3.8914 | 10
3.8903 | 22.5
3.8898 | 10
3.8898 | 4.2
3.8898 | 0.7
3.8891 | 3
3.8888 | 9.3
3.8886 | 7.9
3.8884 | 7.5
3.8881 | 11
3.8879 | 3.7
3.8879 | 16
3.8875 | 2
3.8875 | 12.1
3.887 | 6.5
3.8869 | 17
3.8862 | 8
3.8857 | 2.3
3.8857 | 6
3.8857 | 1.7
3.8857 | 4.5
3.8856 | 17
3.8855 | 12.7
3.8851 | 8.2
3.8847 | 18
3.8847 | 8
3.8844 | 25
3.8843 | 1
3.8843 | 7.1
3.8836 | 10.5
3.8836 | 7.5
3.8833 | 14
3.8826 | 8
3.8819 | 14
3.8816 | 9.1
3.8811 | 15
3.881 | 4.5
3.8809 | 15.7
3.8806 | 5
3.8803 | 3
3.8802 | 9
3.8802 | 9.3
3.8797 | 10.5
3.8795 | 7.5
3.8791 | 25.5
3.8791 | 11
3.8787 | 8
3.8787 | 12.6
3.8783 | 13
3.8777 | 16
3.8773 | 25
3.8773 | 12
3.877 | 2.8
3.8765 | 6.3
3.8755 | 13.5
3.8752 | 5
3.8752 | 3.7
3.8749 | 26
3.8745 | 4
3.8745 | 7.7
3.8745 | 11.4
3.8741 | 7.9
3.8741 | 5.4
3.8741 | 9.2
3.8741 | 11.1
3.8741 | 4.4
3.874 | 9
3.8738 | 12.4
3.8733 | 15
3.8731 | 4.6
3.8728 | 8.5
3.8728 | 9.1
3.8719 | 12
3.8718 | 9
3.8716 | 9
3.8713 | 9
3.8713 | 13
3.871 | 9.7
3.8709 | 15
3.8706 | 14.3
3.8706 | 13
3.8706 | 1
3.8703 | 8
3.8703 | 10.6
3.87 | 9.6
3.8698 | 2.7
3.8693 | 4.2
3.8693 | 8.9
3.8692 | 7.6
3.8692 | 15.6
3.8692 | 15.5
3.869 | 2
3.8689 | 11.7
3.8688 | 6
3.8687 | 8.8
3.8685 | 8.2
3.8683 | 10.5
3.8681 | 11.5
3.8681 | 21
3.8679 | 7.9
3.8678 | 8.3
3.8672 | 0
3.8668 | 3.8
3.8668 | 21
3.8668 | 9.4
3.866 | 5.8
3.8658 | 7.8
3.8654 | 8.6
3.865 | 5.9
3.865 | 22
3.865 | 8
3.8648 | 6.4
3.8647 | 6.2
3.8643 | 7.3
3.864 | 13
3.8639 | 6
3.8639 | 19.2
3.8634 | 10.2
3.8627 | 11
3.8627 | 0.8
3.8624 | 10
3.8622 | 3.7
3.8622 | 11.5
3.8621 | 2
3.8621 | 17.7
3.8614 | 10.5
3.8614 | 13
3.8614 | 6.5
3.8612 | 16
3.8608 | 11.5
3.8608 | 10.8
3.8608 | 15.5
3.8605 | 4.2
3.8604 | 5.5
3.8601 | 20
3.8601 | 6.2
3.86 | 5.7
3.8597 | 22
3.8595 | 3
3.8594 | 5
3.859 | 6.5
3.859 | 12.4
3.8585 | 11.9
3.858 | 9.1
3.858 | 27
3.8576 | 9.9
3.8576 | 7.8
3.8574 | 6
3.8573 | 3.3
3.8573 | 7
3.8573 | 5.9
3.8569 | 5.7
3.8569 | 10
3.8569 | 6
3.8569 | 10.5
3.8568 | 19.4
3.8565 | 1
3.8565 | 8
3.8556 | 5
3.8551 | 18
3.8549 | 6
3.8547 | 13.9
3.8543 | 6.3
3.8543 | 4
3.854 | 18
3.854 | 14.6
3.8535 | 11
3.8535 | 7.3
3.8534 | 8.3
3.8526 | 8.9
3.8526 | 9.8
3.8524 | 5.4
3.8523 | 11.3
3.8522 | 10.5
3.8522 | 5
3.8522 | 5
3.8522 | 6.5
3.852 | 13
3.852 | 15.3
3.8516 | 18
3.8515 | 14
3.8515 | 7.7
3.8515 | 3.2
3.8513 | 2
3.8509 | 4.5
3.8509 | 4.8
3.8508 | 16
3.8504 | 2.3
3.8504 | 7.8
3.8502 | 9
3.8501 | 8.5
3.85 | 15
3.8497 | 12
3.8497 | 7
3.8495 | 3
3.8492 | 13.5
3.8492 | 8.4
3.8491 | 7.5
3.8491 | 17.7
3.8487 | 7.5
3.8479 | 8.9
3.8479 | 8.6
3.8479 | 12
3.8476 | 6.4
3.8475 | 9
3.8471 | 7
3.8468 | 4
3.8468 | 7.9
3.8468 | 6
3.8468 | 24.9
3.8467 | 10.8
3.8462 | 7
3.846 | 5
3.8459 | 4.8
3.8459 | 5.2
3.8457 | 11
3.8457 | 5.6
3.8452 | 8
3.8452 | 14.5
3.8446 | 7.2
3.8446 | 19
3.844 | 14.8
3.8439 | 7
3.8439 | 4
3.8435 | 0
3.8433 | 7
3.8432 | 5.4
3.8432 | 5
3.8432 | 5.6
3.8425 | 18.8
3.8425 | 3.5
3.8424 | 13.5
3.8419 | 6
3.8419 | 10.8
3.8417 | 8
3.8411 | 15.4
3.841 | 3
3.8409 | 3.8
3.8407 | 20.5
3.8406 | 5.8
3.8404 | 5
3.8401 | 3.6
3.84 | 13
3.8398 | 7.5
3.8398 | 4.8
3.8397 | 7.7
3.8397 | 2
3.8392 | 7.6
3.8392 | 6.4
3.8392 | 5.5
3.8391 | 3
3.8389 | 10
3.8385 | 4
3.8385 | 7.5
3.8383 | 10.5
3.8378 | 3.5
3.8372 | 6.1
3.8371 | 10
3.8368 | 7.1
3.8368 | 9.5
3.836 | 5.2
3.8358 | 5.9
3.8358 | 12
3.8358 | 9.9
3.8354 | 5
3.8351 | 24
3.835 | 16.5
3.8336 | 4
3.8334 | 5
3.8331 | 15.5
3.833 | 0.4
3.8326 | 11.3
3.8324 | 6.6
3.8324 | 5.6
3.8324 | 11
3.8319 | 4
3.8316 | 8.2
3.8316 | 8.7
3.8315 | 1.6
3.8314 | 14
3.8304 | 2
3.8298 | 10.5
3.8298 | 15
3.8297 | 8.5
3.8297 | 8
3.8295 | 8.5
3.8294 | 7.2
3.8291 | 13.4
3.8289 | 2
3.8284 | 3.5
3.8284 | 11.9
3.8282 | 11.7
3.8282 | 4.8
3.8281 | 12
3.8278 | 4.7
3.8278 | 1.55
3.8272 | 2
3.827 | 5
3.827 | 9.4
3.8268 | 10
3.8264 | 9
3.826 | 16.4
3.826 | 10.5
3.8256 | 5.3
3.8253 | 3
3.8253 | 4.1
3.8253 | 6
3.825 | 10
3.8248 | 4
3.8248 | 4
3.8247 | 11.95
3.8247 | 9.4
3.8246 | 3.8
3.8244 | 8.7
3.8244 | 13.4
3.8237 | 7.9
3.8236 | 10.6
3.8234 | 27
3.8231 | 10.2
3.823 | 2
3.8229 | 1.9
3.8229 | 4.5
3.8227 | 5
3.8225 | 5.5
3.8224 | 14.6
3.8221 | 5
3.8221 | 10.7
3.8218 | 10
3.8217 | 5.5
3.8217 | 10.5
3.8214 | 12.4
3.8214 | 9.8
3.8214 | 11.2
3.8214 | 8.7
3.821 | 4.5
3.821 | 16
3.821 | 9.1
3.8209 | 1
3.8209 | 5.9
3.8208 | 13.2
3.8203 | 13.5
3.8202 | 17
3.82 | 8
3.82 | 6.5
3.82 | 11.8
3.8197 | 3.7
3.8193 | 4.7
3.8189 | 9.8
3.8185 | 11.2
3.8182 | 17
3.8182 | 0.7
3.8182 | 14
3.8176 | 11.1
3.8173 | 8.8
3.8172 | 8
3.8165 | 7.7
3.8164 | 11.5
3.8164 | 2.3
3.8163 | 10.6
3.8163 | 4
3.816 | 7.4
3.8158 | 10
3.8156 | 3.6
3.8154 | 7.8
3.8151 | 9.3
3.815 | 21
3.8149 | 11.3
3.8147 | 7.5
3.8147 | 11.4
3.8146 | 9.5
3.8146 | 8.3
3.8144 | 0
3.8142 | 10.5
3.8137 | 6.4
3.8137 | 12
3.8136 | 8.5
3.8132 | 10
3.8131 | 7.8
3.8131 | 5.7
3.8131 | 12.4
3.8127 | 9.5
3.8127 | 17.5
3.8125 | 3.4
3.8122 | 9.8
3.8122 | 1.6
3.8116 | 15.8
3.8116 | 11
3.8115 | 5.1
3.8115 | 3.7
3.8113 | 26.4
3.811 | 8.7
3.811 | 16
3.8109 | 7
3.8109 | 7.7
3.8105 | 8.3
3.8104 | 3.5
3.8104 | 6
3.8103 | 8.9
3.81 | 11.6
3.8095 | 6.5
3.8091 | 10.3
3.8091 | 4
3.8091 | 10.6
3.8087 | 8.3
3.8086 | 0
3.8084 | 10.5
3.8084 | 9.9
3.8082 | 14.9
3.8078 | 12.5
3.8077 | 1.85
3.8074 | 2.3
3.8074 | 8.2
3.8073 | 2
3.807 | 2.5
3.807 | 23
3.807 | 10.5
3.8068 | 4.7
3.8064 | 17.5
3.8063 | 6
3.8055 | 3.2
3.8051 | 19.5
3.8048 | 7
3.8048 | 4.5
3.8046 | 7
3.8045 | 14.1
3.8042 | 4.3
3.8041 | 7.8
3.8039 | 9
3.8039 | 7
3.8039 | 15.9
3.8036 | 3
3.8035 | 17.8
3.8033 | 3
3.8028 | 8.6
3.8025 | 3.5
3.8018 | 2
3.8018 | 17.3
3.8017 | 6.5
3.8017 | 5.4
3.8017 | 23.3
3.8011 | 5.5
3.8008 | 8.6
3.8006 | 8
3.8006 | 4
3.8003 | 9
3.7998 | 5.6
3.7995 | 3
3.7992 | 6.8
3.7981 | 9.5
3.7976 | 12.6
3.7974 | 7.1
3.7971 | 4.4
3.7969 | 7.8
3.7968 | 4.2
3.7967 | 9
3.7954 | 14
3.7953 | 5.4
3.7953 | 7
3.7943 | 7
3.7943 | 10
3.7936 | 9.9
3.7933 | 8.2
3.7929 | 18
3.7929 | 10.5
3.7929 | 9.5
3.7929 | 10
3.7924 | 9.2
3.7923 | 15.5
3.792 | 1
3.7919 | 9.2
3.7919 | 6.7
3.7918 | 3.5
3.7916 | 8.5
3.791 | 2
3.791 | 5
3.7909 | 6.7
3.7908 | 15
3.7906 | 4.2
3.7906 | 10.2
3.7906 | 6.8
3.7902 | 7
3.7897 | 7
3.7895 | 4.55
3.7895 | 6
3.7894 | 7.4
3.7893 | 17.6
3.7888 | 3.8
3.7888 | 5
3.7885 | 5.4
3.7885 | 4.5
3.7883 | 17.2
3.7883 | 8.3
3.788 | 11
3.7876 | 23.5
3.7876 | 12.4
3.7876 | 11.5
3.7875 | 3
3.7873 | 8
3.7872 | 4
3.7872 | 10.6
3.7866 | 6.9
3.7862 | 1
3.786 | 7.5
3.7859 | 25
3.7859 | 9.3
3.7853 | 4.5
3.7853 | 8
3.7851 | 6
3.7851 | 10.7
3.7851 | 5.5
3.7843 | 11
3.7838 | 15
3.7837 | 6
3.7834 | 7.9
3.7834 | 6.5
3.7833 | 7.5
3.7831 | 5
3.7831 | 8
3.7826 | 10.7
3.7824 | 11.6
3.7816 | 7.5
3.7816 | 22
3.7814 | 7
3.7814 | 7.1
3.7813 | 22.7
3.781 | 10
3.7807 | 10
3.7803 | 7.9
3.7798 | 9.8
3.7796 | 7
3.7795 | 14.8
3.779 | 5.5
3.779 | 11.5
3.7788 | 9.8
3.7788 | 2
3.7786 | 9.5
3.7786 | 4.5
3.7785 | 20
3.7783 | 18.6
3.7783 | 12.2
3.7782 | 9.9
3.778 | 6.2
3.7776 | 2
3.7772 | 11.5
3.7767 | 10
3.7766 | 6.8
3.7766 | 5.4
3.7766 | 1
3.7766 | 4.4
3.7763 | 13
3.7763 | 20.7
3.7763 | 10
3.7763 | 4.2
3.7762 | 6
3.7762 | 2.3
3.7762 | 4
3.7757 | 6
3.7755 | 3.2
3.7753 | 10.8
3.7752 | 3
3.7752 | 7
3.7751 | 9.8
3.7751 | 9.5
3.7749 | 9.2
3.7749 | 6
3.7748 | 5.7
3.7747 | 10.9
3.7738 | 18
3.7734 | 9.9
3.7728 | 8
3.7728 | 11.3
3.7728 | 6
3.7728 | 4
3.7727 | 4
3.7723 | 12.4
3.7718 | 23
3.7718 | 3
3.7713 | 4
3.7709 | 8.9
3.7707 | 3.9
3.7707 | 3.4
3.7706 | 3.4
3.7706 | 1.9
3.7699 | 5.6
3.7699 | 6.6
3.7698 | 15
3.7693 | 12
3.7692 | 6.7
3.769 | 3.5
3.7686 | 4.3
3.7686 | 4.5
3.7685 | 10.8
3.7685 | 5
3.7683 | 2.3
3.7681 | 5
3.768 | 11.4
3.7679 | 10
3.7666 | 3.9
3.7665 | 3.55
3.7665 | 13.2
3.7659 | 20
3.7659 | 2
3.7659 | 4.2
3.7658 | 14.5
3.7656 | 2
3.7655 | 14
3.7655 | 5.3
3.7645 | 13.9
3.7641 | 3
3.764 | 12.2
3.7633 | 11.2
3.7632 | 13.5
3.7632 | 1.8
3.7627 | 20.3
3.7626 | 7.5
3.7626 | 9.5
3.7623 | 8.2
3.762 | 16.2
3.762 | 11.3
3.7617 | 15.4
3.7614 | 6.4
3.7611 | 6.5
3.7611 | 5.7
3.7609 | 15.3
3.7607 | 17
3.7605 | 8.2
3.7605 | 10
3.7602 | 0
3.76 | 8
3.7591 | 16.5
3.7591 | 5
3.759 | 4
3.7589 | 11.5
3.7587 | 2.9
3.7587 | 6
3.7587 | 22.4
3.7584 | 6.5
3.7583 | 10.7
3.7583 | 6.5
3.7581 | 5
3.7581 | 7
3.7578 | 0
3.7577 | 5
3.7574 | 4.6
3.7574 | 1
3.7573 | 8.5
3.7571 | 5
3.757 | 11.2
3.757 | 4
3.7566 | 22.7
3.7563 | 10.5
3.7563 | 7.8
3.7563 | 2.3
3.7562 | 9.1
3.756 | 5.7
3.756 | 10.7
3.7559 | 10
3.7559 | 7
3.7557 | 1
3.7556 | 7
3.7552 | 5.8
3.755 | 6.3
3.755 | 9.5
3.7545 | 11.8
3.7545 | 15.5
3.7537 | 16
3.7537 | 7.2
3.7537 | 5.5
3.7525 | 8
3.7524 | 5
3.7524 | 11.2
3.7523 | 6.5
3.7522 | 20.3
3.7517 | 6.5
3.7514 | 8.5
3.7514 | 12.7
3.7509 | 4.2
3.7509 | 5
3.7501 | 5.1
3.7501 | 9.2
3.7496 | 8.4
3.7496 | 12.5
3.7496 | 14
3.7496 | 14.2
3.7495 | 5.6
3.7495 | 4
3.7489 | 10.5
3.7488 | 6.5
3.7486 | 16
3.7483 | 11
3.7483 | 19
3.7478 | 5
3.7472 | 9.2
3.7469 | 9.4
3.7469 | 5.3
3.7467 | 5.2
3.7466 | 14.6
3.7465 | 9
3.7461 | 5
3.7458 | 6.9
3.7449 | 2.5
3.7449 | 19
3.7444 | 8.5
3.7442 | 16.5
3.744 | 3.5
3.744 | 9
3.7431 | 9.8
3.743 | 2
3.7417 | 9.1
3.7408 | 10.3
3.7407 | 13
3.7404 | 3
3.74 | 7
3.7398 | 23
3.7398 | 4.5
3.7394 | 66
3.7392 | 9.6
3.7392 | 3.6
3.739 | 21.5
3.7387 | 10.2
3.7387 | 1
3.7387 | 11.6
3.7383 | 9.9
3.7383 | 8.7
3.7382 | 5
3.7382 | 9.8
3.7382 | 10
3.7382 | 8.4
3.7382 | 13
3.738 | 6.7
3.738 | 9.9
3.738 | 9.2
3.738 | 9.3
3.7379 | 10.1
3.7373 | 7.9
3.7372 | 7.5
3.7371 | 11.7
3.7371 | 16.6
3.7371 | 16.7
3.7365 | 13
3.7362 | 12
3.7362 | 10.8
3.7358 | 2.9
3.7358 | 7.5
3.7353 | 2.6
3.7341 | 8
3.7338 | 4.4
3.7338 | 7.6
3.7334 | 3.9
3.7327 | 7.2
3.7324 | 2.5
3.7324 | 5.4
3.7321 | 18
3.7319 | 10
3.7313 | 12.5
3.7313 | 12.5
3.7313 | 6.5
3.7312 | 7.4
3.7306 | 14
3.7306 | 11.4
3.7299 | 5
3.7299 | 6.6
3.7299 | 2
3.7296 | 26
3.729 | 2
3.7289 | 3.2
3.7286 | 8.2
3.7281 | 6.8
3.7275 | 7.9
3.7274 | 12.5
3.7273 | 3.4
3.7271 | 27
3.7269 | 16
3.7257 | 4.5
3.7257 | 2
3.7256 | 6.3
3.7254 | 9
3.7254 | 13.7
3.7251 | 3.6
3.7248 | 6.5
3.7247 | 9.4
3.7236 | 6.3
3.7234 | 16
3.7234 | 12.3
3.7232 | 11.9
3.7228 | 1
3.7227 | 11.2
3.7222 | 5.4
3.722 | 12
3.7218 | 6.3
3.7218 | 6.7
3.7215 | 3
3.7215 | 13.6
3.7214 | 4
3.721 | 5.1
3.7207 | 8.2
3.7205 | 0
3.7204 | 7.6
3.72 | 11.4
3.7198 | 2
3.719 | 16.2
3.719 | 5.7
3.719 | 8.2
3.7187 | 7.2
3.7184 | 4
3.718 | 8.5
3.718 | 4
3.7179 | 12
3.7179 | 14
3.7174 | 5
3.7172 | 4.2
3.7167 | 7.6
3.7166 | 12.1
3.7165 | 21
3.7165 | 8.6
3.7165 | 12.9
3.7164 | 2
3.7163 | 2
3.7158 | 12.5
3.7156 | 5.8
3.7156 | 9.3
3.7155 | 2.9
3.7155 | 2.3
3.7155 | 14
3.7153 | 9.2
3.7137 | 9.7
3.7137 | 7
3.7136 | 12.4
3.7133 | 8
3.7126 | 12.8
3.7125 | 12
3.7123 | 12
3.712 | 5.5
3.7119 | 21.8
3.7118 | 10
3.7112 | 9
3.7112 | 9.9
3.711 | 13.5
3.7109 | 15
3.7109 | 13
3.7108 | 3
3.7107 | 10
3.7106 | 11.3
3.7105 | 2.3
3.7104 | 0
3.7103 | 9
3.7102 | 2
3.7099 | 5.6
3.7099 | 10
3.7099 | 10
3.7098 | 7.5
3.7096 | 1
3.7095 | 7
3.7094 | 1.4
3.7094 | 11.3
3.7092 | 10.5
3.7091 | 24.5
3.7087 | 11.8
3.7085 | 22.3
3.7085 | 7
3.7078 | 3
3.7078 | 10.8
3.7072 | 10.6
3.7072 | 3.8
3.7065 | 6.4
3.7065 | 12
3.7064 | 8
3.7056 | 11
3.705 | 9.8
3.7046 | 3.4
3.7045 | 23
3.7045 | 8.1
3.7038 | 14.2
3.7036 | 6.6
3.7036 | 9.5
3.7036 | 13
3.7036 | 8.5
3.7032 | 12
3.7031 | 11.6
3.7031 | 12
3.7029 | 14.7
3.7029 | 8.3
3.7028 | 10
3.702 | 5.9
3.7018 | 7.2
3.7014 | 9.9
3.7006 | 6
3.7 | 10.2
3.6999 | 15
3.6999 | 22
3.6998 | 5
3.6997 | 8.8
3.6997 | 8.6
3.6997 | 4.1
3.6997 | 10.7
3.6993 | 6.9
3.6992 | 5.1
3.6992 | 16
3.6987 | 9.4
3.6984 | 9.9
3.6984 | 12.2
3.698 | 10.3
3.6979 | 6.1
3.6979 | 21
3.6978 | 12.5
3.6975 | 18
3.6973 | 8.5
3.6973 | 7
3.6971 | 2
3.6968 | 11
3.6968 | 8
3.6966 | 3
3.6964 | 9
3.6964 | 17.5
3.6964 | 25
3.6963 | 13.8
3.6961 | 21
3.6961 | 4.8
3.6961 | 11
3.6961 | 12.6
3.6951 | 9.1
3.695 | 13
3.6947 | 5
3.6946 | 6.4
3.6944 | 10.5
3.6943 | 12
3.6939 | 5.8
3.6936 | 9
3.6923 | 2.4
3.6921 | 10.8
3.6917 | 12.1
3.6912 | 6
3.6912 | 8
3.6908 | 8.5
3.6907 | 7.5
3.6904 | 8.9
3.6895 | 10.25
3.6893 | 10.5
3.6893 | 24.6
3.6893 | 7.9
3.6893 | 13.1
3.6888 | 8.2
3.6885 | 2.8
3.6877 | 3.9
3.6875 | 5
3.6872 | 1.85
3.6867 | 13.5
3.6863 | 22
3.6863 | 2
3.6862 | 9.6
3.686 | 19.9
3.6858 | 3.8
3.6857 | 9
3.6855 | 10
3.6849 | 14
3.6849 | 3
3.6849 | 15.5
3.6841 | 7.5
3.6841 | 2
3.6836 | 18.5
3.6824 | 13.7
3.682 | 11.6
3.6815 | 1.8
3.6815 | 5.3
3.681 | 6.2
3.681 | 6.3
3.681 | 11
3.681 | 8.1
3.681 | 24
3.6809 | 3.9
3.6806 | 8
3.6806 | 4.8
3.6806 | 10
3.6806 | 3.5
3.6806 | 23
3.6806 | 22
3.6805 | 9.9
3.6805 | 7.3
3.6804 | 9
3.6804 | 6.5
3.6797 | 24
3.6793 | 12.2
3.6789 | 17
3.6782 | 9.5
3.6777 | 11.7
3.6776 | 3
3.6776 | 2.7
3.6776 | 5.4
3.6776 | 7.8
3.6776 | 4
3.6776 | 8.8
3.6771 | 11
3.6768 | 8.7
3.6767 | 8.8
3.6766 | 5.3
3.6761 | 13.2
3.675 | 9.5
3.675 | 20.5
3.675 | 22
3.675 | 22
3.6749 | 9.2
3.6742 | 3
3.6735 | 4
3.6733 | 3.3
3.6732 | 19.2
3.6725 | 12.3
3.6725 | 3
3.6725 | 9
3.6716 | 16.8
3.6715 | 7.6
3.6715 | 11.4
3.6712 | 14
3.6708 | 10.5
3.6708 | 10
3.6708 | 21
3.6708 | 7.5
3.6705 | 23
3.6701 | 5.5
3.6699 | 6.5
3.6698 | 9.9
3.6695 | 16.8
3.6687 | 11.9
3.6687 | 12
3.6685 | 16.5
3.6685 | 12.5
3.6684 | 3.3
3.6681 | 11.9
3.668 | 2.2
3.668 | 3
3.6679 | 11.3
3.6678 | 7.6
3.6672 | 9
3.6672 | 20.5
3.6672 | 3.1
3.667 | 8.5
3.6663 | 18
3.6663 | 10.5
3.6661 | 4.3
3.666 | 6.1
3.6659 | 12.3
3.6659 | 9.4
3.6659 | 0
3.6651 | 10.7
3.6651 | 4.3
3.665 | 11.8
3.665 | 15.7
3.6646 | 12.8
3.6643 | 3.4
3.6642 | 1
3.6639 | 6.9
3.6637 | 4.3
3.663 | 10
3.662 | 10.5
3.6619 | 15.1
3.6614 | 17
3.6614 | 22.1
3.6614 | 11.4
3.6614 | 10.4
3.6614 | 1
3.6613 | 1
3.661 | 9
3.6609 | 22.5
3.6606 | 8.7
3.6606 | 10.4
3.6606 | 13
3.6602 | 11.4
3.66 | 9.2
3.66 | 9
3.6599 | 27
3.6599 | 8.7
3.6594 | 9
3.6594 | 7
3.6594 | 3
3.6586 | 9.4
3.6585 | 7.2
3.6585 | 7.9
3.6585 | 12.4
3.6579 | 16.2
3.6579 | 12.4
3.6577 | 7.6
3.6574 | 14.5
3.657 | 6
3.6568 | 4.2
3.6567 | 3
3.6567 | 11.3
3.6565 | 4.8
3.6564 | 4
3.6563 | 10.3
3.6561 | 11
3.6557 | 6
3.6556 | 5.7
3.6548 | 24
3.6547 | 12
3.6547 | 9.7
3.6547 | 15
3.6545 | 10.2
3.6543 | 5.4
3.6543 | 5.2
3.6543 | 2
3.6543 | 2
3.6542 | 7
3.6537 | 2.3
3.6534 | 8
3.6534 | 20
3.6533 | 5.9
3.6532 | 8.9
3.6532 | 8
3.6529 | 10
3.6527 | 5.1
3.6522 | 5
3.652 | 4
3.6517 | 8.6
3.6509 | 11.8
3.6508 | 20
3.6508 | 8
3.6506 | 19
3.6502 | 4.5
3.6497 | 14.1
3.6496 | 3
3.6493 | 16.1
3.6487 | 3.6
3.6486 | 16
3.6484 | 9.2
3.6484 | 1.6
3.6479 | 2
3.6479 | 19
3.6479 | 10.1
3.6479 | 3.9
3.6476 | 4
3.6468 | 8.5
3.6466 | 5.9
3.6466 | 5.1
3.6463 | 7.6
3.6461 | 2.8
3.6461 | 5
3.6455 | 9.7
3.6448 | 12.1
3.6445 | 9
3.6437 | 10.9
3.6437 | 24
3.6437 | 4.2
3.6434 | 6.6
3.6433 | 12.2
3.643 | 6.3
3.6427 | 5.5
3.6427 | 8.9
3.6421 | 6.4
3.642 | 10.7
3.6417 | 3
3.6417 | 17
3.6412 | 8.8
3.6411 | 8
3.6411 | 4.1
3.6407 | 5
3.6406 | 12.7
3.6402 | 10.6
3.6398 | 17.6
3.6397 | 11.6
3.6395 | 5.6
3.6391 | 13.4
3.6381 | 14
3.6381 | 11
3.6379 | 5.6
3.6377 | 4.5
3.6375 | 5.7
3.6373 | 2
3.6373 | 10.4
3.6367 | 10.3
3.6366 | 4.2
3.6365 | 9.5
3.6361 | 8.4
3.636 | 5.2
3.6358 | 10.8
3.6357 | 8.1
3.6356 | 15
3.6346 | 3.5
3.6344 | 5.1
3.6338 | 7
3.6331 | 5.1
3.6328 | 3.8
3.6328 | 14
3.6328 | 10
3.6325 | 6.3
3.6325 | 10
3.6325 | 10.2
3.6325 | 12.8
3.6324 | 2
3.6324 | 2
3.6324 | 6.5
3.6321 | 7.7
3.6321 | 11
3.632 | 9.8
3.6318 | 8
3.6316 | 4.3
3.6313 | 8
3.6311 | 11.5
3.631 | 5.8
3.6308 | 0
3.6306 | 24
3.6297 | 3.9
3.6296 | 2.1
3.6296 | 2.1
3.6294 | 8.5
3.6293 | 17.5
3.6292 | 11
3.6291 | 3.7
3.629 | 7.2
3.629 | 5.6
3.629 | 6.3
3.6284 | 9.5
3.628 | 5
3.6277 | 7.7
3.6277 | 9.8
3.6276 | 9.9
3.6266 | 9.8
3.6264 | 13
3.6261 | 10
3.6257 | 13.4
3.6248 | 2
3.6244 | 9.1
3.6244 | 12
3.6244 | 12
3.6243 | 22.3
3.6241 | 9.5
3.624 | 11.2
3.6236 | 8.5
3.623 | 6
3.623 | 7.3
3.623 | 9
3.6224 | 10.1
3.6222 | 8.1
3.6222 | 11.5
3.6221 | 6.7
3.622 | 9.7
3.622 | 19.2
3.6215 | 5.8
3.6215 | 13
3.6212 | 8.8
3.621 | 18
3.6208 | 9.8
3.6208 | 7.8
3.6201 | 6.2
3.6201 | 5.6
3.62 | 2.7
3.6197 | 5.8
3.6177 | 13.2
3.6175 | 2
3.617 | 6.3
3.6159 | 8.7
3.6156 | 10.9
3.6156 | 9
3.6153 | 3
3.6152 | 2.9
3.6149 | 7.2
3.6148 | 7.8
3.6146 | 6.5
3.6143 | 1
3.614 | 12.2
3.6139 | 0
3.6138 | 6.2
3.6136 | 10.5
3.6136 | 8
3.6134 | 11
3.6133 | 5
3.6126 | 8.4
3.6126 | 4.2
3.6124 | 14.2
3.6119 | 5.4
3.6116 | 22
3.6114 | 5.8
3.611 | 11
3.6105 | 6
3.6105 | 13.6
3.6105 | 19
3.6102 | 4
3.6102 | 2
3.61 | 12
3.6097 | 10.3
3.6092 | 7.9
3.6092 | 4.4
3.6092 | 3.9
3.609 | 11
3.6089 | 12.2
3.6071 | 14.4
3.6069 | 2
3.6069 | 2
3.6065 | 5.7
3.6061 | 3.8
3.6058 | 9.4
3.6054 | 10.6
3.6046 | 2
3.6046 | 11
3.6045 | 17
3.6045 | 17
3.6043 | 6.6
3.604 | 4.2
3.604 | 0
3.6038 | 16.5
3.6033 | 16.4
3.6033 | 7.5
3.6032 | 3.1
3.6031 | 7
3.603 | 9.7
3.6023 | 8.2
3.6017 | 8.7
3.6017 | 7.6
3.6012 | 5.6
3.6003 | 7
3.5995 | 10
3.5995 | 10.6
3.5994 | 5
3.5989 | 4.7
3.5981 | 1.2
3.5976 | 8.3
3.5973 | 10
3.5969 | 11.2
3.5968 | 17
3.5967 | 10.2
3.5963 | 9.3
3.596 | 4.2
3.5955 | 2.15
3.5948 | 8.8
3.5947 | 27
3.5947 | 8.4
3.5941 | 4.4
3.594 | 7.1
3.594 | 5.9
3.5939 | 8.9
3.5932 | 8
3.5931 | 2.3
3.5924 | 12.2
3.5923 | 1
3.5915 | 6.5
3.5915 | 13.1
3.591 | 9.1
3.5908 | 5.1
3.5907 | 1
3.5907 | 6.6
3.59 | 9.8
3.5896 | 18
3.5894 | 10.5
3.589 | 10
3.5889 | 16
3.5882 | 13.4
3.5879 | 3.5
3.5873 | 12.8
3.5873 | 11
3.5872 | 11.6
3.5864 | 4.3
3.5862 | 17.9
3.586 | 6.4
3.586 | 4.2
3.5857 | 11.5
3.5851 | 6.3
3.5844 | 5
3.5841 | 4.7
3.5836 | 3
3.5836 | 14.5
3.5836 | 25.5
3.5835 | 23
3.5835 | 9.2
3.5833 | 1
3.5833 | 9.3
3.5832 | 8
3.5829 | 11.8
3.5825 | 10.3
3.5825 | 3.8
3.5823 | 4
3.5823 | 4.1
3.582 | 7.1
3.5818 | 3.4
3.5818 | 3.9
3.5816 | 9.5
3.5816 | 15.8
3.5815 | 6.5
3.58 | 10.5
3.5799 | 2
3.5799 | 10
3.5799 | 7.9
3.5797 | 12.8
3.5797 | 19.7
3.5793 | 6.3
3.5793 | 10
3.5792 | 10
3.5784 | 6.4
3.5784 | 2.3
3.5784 | 10
3.5782 | 7
3.577 | 15.6
3.577 | 13
3.5765 | 2.9
3.5765 | 11
3.5765 | 10.3
3.5765 | 5
3.5764 | 12.4
3.5764 | 19
3.5764 | 0
3.5761 | 5.7
3.5759 | 15.2
3.5759 | 14.2
3.5756 | 12.2
3.5755 | 9.5
3.5743 | 4
3.5734 | 16.1
3.5734 | 5
3.5734 | 5
3.5732 | 2.5
3.5729 | 8
3.5725 | 8.5
3.5719 | 3
3.5719 | 8.1
3.5716 | 6.6
3.5716 | 13.4
3.5716 | 8.9
3.5715 | 3.5
3.5715 | 6.3
3.5712 | 6.3
3.5711 | 3.1
3.5708 | 3
3.5692 | 6.5
3.5685 | 13
3.5685 | 8.2
3.5684 | 9.4
3.5678 | 12.5
3.5675 | 7
3.5671 | 2.8
3.5666 | 12.8
3.5665 | 9.9
3.5662 | 7
3.5662 | 9.5
3.5659 | 24
3.5659 | 20
3.5657 | 7.6
3.5657 | 9
3.5657 | 15
3.5657 | 9.8
3.5653 | 13
3.5652 | 3
3.5645 | 7.5
3.564 | 3
3.564 | 21
3.5639 | 10
3.5638 | 10.1
3.5633 | 4.1
3.5633 | 7.1
3.5626 | 7.9
3.5617 | 9.9
3.5614 | 9.1
3.561 | 5.1
3.561 | 11.6
3.5607 | 19
3.5604 | 2
3.5604 | 10.9
3.5603 | 7.6
3.5601 | 14.2
3.5601 | 6.7
3.5597 | 16
3.5592 | 9.5
3.5591 | 5.1
3.5588 | 12
3.5586 | 6.2
3.5586 | 10.3
3.5582 | 16.7
3.5575 | 4.1
3.5572 | 11
3.5568 | 12.4
3.5561 | 6.2
3.556 | 8
3.5556 | 1
3.5556 | 5
3.5556 | 12.3
3.5553 | 12.4
3.5551 | 25
3.555 | 10.8
3.5547 | 16
3.5545 | 2
3.5545 | 4.2
3.5545 | 10.4
3.5545 | 9.4
3.5544 | 8.5
3.5544 | 10
3.5544 | 8.2
3.5544 | 11
3.5539 | 8.5
3.5536 | 17
3.5536 | 10
3.5529 | 22
3.5524 | 12.3
3.5524 | 11.2
3.5522 | 8.4
3.5522 | 24
3.5519 | 5.6
3.5518 | 2
3.5517 | 12.3
3.5516 | 16
3.551 | 8.5
3.551 | 2.3
3.5509 | 6.2
3.5509 | 3.9
3.5508 | 7.1
3.5502 | 4.6
3.55 | 5.2
3.55 | 7.5
3.5498 | 6.5
3.5496 | 12.8
3.5496 | 24
3.5495 | 7.6
3.549 | 17.5
3.5487 | 7
3.5486 | 12.6
3.5481 | 10
3.547 | 11.2
3.5467 | 13.2
3.5467 | 6.2
3.5465 | 1.2
3.546 | 8.3
3.5458 | 2
3.5457 | 7.5
3.5455 | 1
3.5451 | 0
3.5449 | 7.9
3.5438 | 5
3.5437 | 5
3.5434 | 4.2
3.5431 | 18.6
3.5431 | 9.8
3.5431 | 11.3
3.5431 | 10.5
3.5431 | 0.6
3.5431 | 5
3.5424 | 11
3.5422 | 10.9
3.5422 | 17
3.5422 | 10.3
3.5421 | 4.1
3.5421 | 13.1
3.5416 | 5.6
3.5413 | 19.2
3.5411 | 11
3.541 | 4.8
3.5407 | 4
3.5402 | 6.7
3.5395 | 2
3.5391 | 11.2
3.5389 | 7.3
3.5389 | 5.9
3.5389 | 5.5
3.5387 | 5.5
3.5387 | 5.7
3.5385 | 22.05
3.5384 | 8
3.5382 | 2
3.5375 | 8.6
3.5374 | 9.2
3.5373 | 7.9
3.5373 | 7.7
3.5372 | 7.4
3.5372 | 0
3.5371 | 2
3.5365 | 2
3.5362 | 5.7
3.5361 | 8.5
3.536 | 12.4
3.5359 | 8.2
3.5355 | 3
3.5355 | 11.5
3.5342 | 6.6
3.5338 | 8.5
3.5335 | 2.8
3.5335 | 2.3
3.5334 | 3.9
3.5328 | 10.9
3.5328 | 8.5
3.5326 | 1
3.5326 | 2
3.5326 | 13
3.5326 | 7.3
3.5325 | 7
3.5321 | 8
3.5319 | 11.5
3.5317 | 4
3.5316 | 2
3.5312 | 21.3
3.531 | 10
3.5305 | 5
3.53 | 9.2
3.5293 | 9.9
3.529 | 6.4
3.529 | 19.5
3.5287 | 19.6
3.5284 | 6
3.5284 | 5.5
3.5276 | 11.5
3.5276 | 8.5
3.5274 | 15.4
3.527 | 6
3.527 | 3.9
3.527 | 4.8
3.5267 | 18
3.5267 | 3
3.5263 | 12.1
3.5258 | 5.4
3.5257 | 0
3.5249 | 4.1
3.5248 | 3
3.5248 | 10
3.5245 | 8
3.5245 | 12
3.5245 | 9
3.5243 | 2
3.5243 | 9.8
3.5236 | 5.5
3.5234 | 9.5
3.523 | 1
3.523 | 15.6
3.523 | 9.8
3.5228 | 9.8
3.522 | 10
3.5216 | 5.6
3.5213 | 5.7
3.5209 | 8.5
3.5208 | 0
3.5203 | 19.2
3.5203 | 9
3.5202 | 7.2
3.5202 | 14
3.5199 | 10.4
3.5199 | 12.6
3.5195 | 11.6
3.5189 | 11.4
3.5185 | 2
3.5185 | 26
3.5171 | 10.6
3.5157 | 10.2
3.5154 | 8.2
3.5152 | 8
3.515 | 11.5
3.5147 | 15.4
3.5147 | 7
3.5144 | 8.9
3.5144 | 10.1
3.5143 | 16
3.5143 | 7.5
3.514 | 6
3.514 | 8.3
3.5138 | 2.1
3.513 | 13.5
3.5124 | 29
3.5113 | 1
3.511 | 4.1
3.511 | 2.4
3.5104 | 12
3.5101 | 21
3.5099 | 8.4
3.5099 | 7.7
3.5099 | 5.2
3.5097 | 8.3
3.5095 | 2.6
3.5093 | 4.2
3.5092 | 3
3.5086 | 9.7
3.5081 | 8.3
3.5072 | 4
3.5068 | 12.1
3.5066 | 10.2
3.5065 | 1
3.5065 | 0
3.5065 | 11.5
3.5061 | 12.5
3.5057 | 20.5
3.5054 | 14
3.5051 | 11.2
3.505 | 4.2
3.5047 | 2.6
3.5045 | 10
3.5045 | 12.5
3.5044 | 18
3.5041 | 15.1
3.5041 | 7.3
3.5035 | 18
3.5032 | 9
3.503 | 22.6
3.5027 | 4.4
3.5023 | 10
3.5019 | 7.2
3.5012 | 7.5
3.501 | 16.7
3.5007 | 14.1
3.4999 | 15.7
3.4999 | 5.8
3.4997 | 2.3
3.4994 | 8.8
3.4993 | 0
3.499 | 10.5
3.499 | 3
3.4988 | 5.6
3.4987 | 6
3.4986 | 9.9
3.4983 | 10.5
3.4981 | 8.1
3.498 | 10.8
3.498 | 4.7
3.4979 | 8.5
3.4978 | 0
3.4975 | 8
3.4974 | 4.1
3.4973 | 8
3.4973 | 12.4
3.4973 | 0
3.497 | 0
3.4969 | 6.6
3.4969 | 6
3.4967 | 10.4
3.4961 | 5
3.4959 | 7.6
3.4959 | 16
3.4959 | 21
3.4955 | 6
3.4955 | 13.2
3.4951 | 11.3
3.4951 | 8.1
3.4946 | 12.4
3.4943 | 10.4
3.4939 | 9.2
3.4934 | 2
3.4928 | 2.3
3.4928 | 10.4
3.4926 | 5.6
3.492 | 12.3
3.4914 | 8.9
3.4913 | 16
3.4908 | 13.4
3.4908 | 8.3
3.4903 | 4.9
3.4901 | 7.6
3.4901 | 14.6
3.4897 | 18
3.4894 | 10.5
3.4893 | 1.8
3.489 | 3
3.489 | 11
3.489 | 15.3
3.4889 | 1
3.4888 | 3.1
3.4887 | 12.8
3.4887 | 16
3.4887 | 8.6
3.4883 | 6
3.4883 | 11.5
3.4882 | 3.25
3.4882 | 0.6
3.488 | 12.4
3.4858 | 16
3.4855 | 4.7
3.4855 | 8.1
3.4853 | 6
3.4849 | 7.5
3.4842 | 20.5
3.4839 | 7.5
3.4839 | 14.6
3.4836 | 8.9
3.4835 | 8.5
3.4832 | 2
3.4825 | 9
3.4817 | 1
3.4812 | 5.2
3.4797 | 0
3.4796 | 0
3.4796 | 7
3.4793 | 26
3.4784 | 12.3
3.4781 | 4.2
3.4781 | 4.2
3.4781 | 4
3.4781 | 5
3.4774 | 9.2
3.4772 | 21
3.477 | 9.2
3.477 | 1
3.4768 | 3
3.4764 | 9.3
3.476 | 4
3.4757 | 3.1
3.4754 | 1
3.4751 | 10.5
3.475 | 3
3.4745 | 0
3.4738 | 9.5
3.4728 | 10.6
3.4726 | 8.7
3.4725 | 11
3.4723 | 7
3.4718 | 13
3.4712 | 12.7
3.471 | 5.2
3.4709 | 3.5
3.4709 | 5
3.4709 | 8.1
3.4702 | 12
3.4702 | 12.6
3.47 | 14.2
3.47 | 10.7
3.4691 | 5
3.4691 | 12
3.4685 | 22
3.4682 | 11.8
3.4675 | 8.5
3.4675 | 11.3
3.4675 | 13
3.4672 | 6
3.4664 | 1
3.4662 | 2.6
3.4655 | 11
3.465 | 13
3.4646 | 6.2
3.4646 | 20.8
3.4644 | 9.4
3.4642 | 3
3.464 | 10.3
3.4639 | 12.2
3.4636 | 10.6
3.4633 | 15.5
3.4622 | 9.7
3.4621 | 15.1
3.462 | 5.4
3.4614 | 16
3.461 | 15.6
3.4608 | 19.3
3.4606 | 7.2
3.4603 | 26.2
3.4601 | 0
3.4599 | 3.5
3.4587 | 4.4
3.4587 | 5.2
3.4587 | 9.9
3.4578 | 6
3.4575 | 12.5
3.4572 | 11
3.4557 | 5
3.4557 | 2
3.4554 | 17
3.4548 | 10
3.4547 | 13.4
3.4541 | 5.7
3.4529 | 5
3.4529 | 11
3.4524 | 11.6
3.4522 | 7
3.4522 | 3.3
3.452 | 0
3.4517 | 9.5
3.4509 | 9
3.4509 | 3
3.4505 | 6
3.4496 | 10.4
3.4493 | 6.5
3.4487 | 15.2
3.4487 | 17
3.4476 | 9
3.4476 | 1
3.4473 | 17.5
3.447 | 1.9
3.447 | 3
3.4468 | 12
3.4468 | 13
3.4457 | 12.5
3.4453 | 10
3.4451 | 9.4
3.4451 | 6.4
3.4446 | 11.2
3.4442 | 11.8
3.4428 | 12.4
3.4427 | 19.2
3.4425 | 4.6
3.4424 | 16
3.4424 | 8.7
3.4423 | 10.3
3.4421 | 7
3.4421 | 7
3.4419 | 3
3.4419 | 9.1
3.4418 | 3
3.4417 | 3.2
3.4412 | 15.8
3.4411 | 17
3.4411 | 23
3.4411 | 6.4
3.4403 | 14.1
3.4403 | 12.5
3.4402 | 3.3
3.4393 | 8
3.4391 | 17
3.439 | 4.4
3.4386 | 8.6
3.4385 | 8
3.4384 | 7.6
3.4381 | 10
3.4376 | 10
3.4376 | 12.5
3.4374 | 11.8
3.4371 | 15.7
3.4367 | 12.6
3.4365 | 18
3.4364 | 7
3.4361 | 5.2
3.4357 | 6.7
3.4353 | 9
3.4352 | 12.1
3.4345 | 11
3.4345 | 4.5
3.4341 | 11.5
3.433 | 9.9
3.4326 | 4.4
3.4326 | 7
3.4325 | 2
3.4323 | 6.5
3.4323 | 8
3.4315 | 21
3.4313 | 9.2
3.4313 | 26
3.4308 | 8
3.4307 | 5.7
3.4304 | 19
3.43 | 5.7
3.4287 | 15.6
3.4287 | 10
3.4285 | 3.5
3.4277 | 12.8
3.4271 | 12
3.4269 | 3.1
3.4268 | 7.5
3.4257 | 7.7
3.4254 | 6
3.425 | 5.4
3.425 | 11.1
3.4248 | 10.9
3.4244 | 11.05
3.4237 | 5.5
3.4237 | 11.1
3.4235 | 23
3.4235 | 11
3.4228 | 4.2
3.4228 | 6.7
3.4228 | 11.1
3.4223 | 13.2
3.4223 | 11.2
3.4218 | 12.6
3.4217 | 14
3.4213 | 20
3.4206 | 7.5
3.4196 | 11.9
3.4191 | 8
3.419 | 2
3.419 | 2
3.4181 | 8.2
3.4179 | 10
3.4171 | 6
3.4163 | 1
3.4163 | 4
3.415 | 5.5
3.4146 | 11.5
3.4142 | 6.7
3.4135 | 17.2
3.4134 | 7.9
3.413 | 10.5
3.4109 | 7
3.4106 | 12
3.4103 | 9.3
3.4102 | 8
3.4099 | 12.5
3.4097 | 12.4
3.4097 | 0
3.4095 | 8
3.4093 | 11.3
3.4089 | 10
3.4086 | 11.4
3.4086 | 15.3
3.4079 | 8.6
3.4073 | 13.6
3.4069 | 4.4
3.4065 | 6.8
3.4061 | 0
3.4061 | 2
3.4058 | 20.3
3.4058 | 6.1
3.4045 | 8
3.4042 | 17
3.4042 | 7.5
3.4039 | 11
3.4038 | 2.3
3.4034 | 9.7
3.4032 | 5.8
3.4032 | 13.5
3.4032 | 15
3.4031 | 5.5
3.4028 | 6.1
3.4028 | 4.5
3.4026 | 6.1
3.4019 | 17
3.4017 | 7.4
3.4008 | 7
3.4008 | 11.2
3.4006 | 3.9
3.4003 | 12.9
3.3999 | 13
3.3998 | 7.5
3.3996 | 9
3.399 | 2.9
3.3989 | 6.8
3.3989 | 11.5
3.3986 | 9.5
3.3985 | 7.2
3.3982 | 9
3.3968 | 10.1
3.3967 | 15.5
3.3966 | 2
3.3962 | 5.9
3.3961 | 7
3.3944 | 10.7
3.3928 | 11
3.3926 | 8.3
3.3926 | 8.6
3.3923 | 13.5
3.3922 | 8.4
3.392 | 8.4
3.3919 | 22
3.3917 | 14
3.3917 | 15.5
3.3915 | 5
3.3908 | 3.4
3.3908 | 3.8
3.3903 | 11
3.3901 | 6.5
3.3901 | 8.9
3.39 | 6
3.3894 | 3
3.3893 | 7.5
3.3888 | 9.9
3.3881 | 1.6
3.3872 | 5
3.3872 | 6.3
3.3869 | 10.5
3.3857 | 10
3.3855 | 5.8
3.3854 | 19.2
3.3854 | 18
3.3849 | 9.9
3.3843 | 7
3.384 | 22
3.3836 | 7.9
3.3826 | 4.9
3.3813 | 7
3.3813 | 22
3.3806 | 4.8
3.3803 | 9.5
3.3797 | 5.4
3.3797 | 20.1
3.3797 | 7.3
3.379 | 9.5
3.3789 | 7.3
3.3786 | 9
3.3786 | 10.2
3.3785 | 9.1
3.3784 | 10.6
3.3781 | 4.1
3.3781 | 4
3.3781 | 7.3
3.378 | 10.2
3.378 | 7.5
3.3778 | 4.7
3.3773 | 6
3.3773 | 5.4
3.3765 | 7.5
3.3755 | 17.9
3.3748 | 1
3.3746 | 13
3.3743 | 5.2
3.3741 | 10.5
3.374 | 2
3.3738 | 4.5
3.3737 | 6.9
3.3728 | 4.5
3.3726 | 10.5
3.3724 | 11
3.3724 | 12
3.371 | 1.2
3.3705 | 10
3.3705 | 0
3.3701 | 6
3.3699 | 12
3.3697 | 12
3.3689 | 3.2
3.3679 | 3.5
3.3676 | 6.2
3.3672 | 9
3.367 | 12.8
3.367 | 14
3.367 | 10.6
3.3667 | 9.9
3.3666 | 3.3
3.3666 | 9.1
3.3656 | 6.9
3.3655 | 3
3.3653 | 6
3.3653 | 9.5
3.3652 | 20.8
3.3647 | 9.3
3.3644 | 9.7
3.3637 | 9.5
3.3634 | 8.7
3.3621 | 5.4
3.3621 | 2.5
3.3612 | 10.7
3.3607 | 12.8
3.3604 | 11
3.3595 | 5.9
3.3595 | 7.1
3.3595 | 7
3.3594 | 10
3.3586 | 8.2
3.3583 | 11
3.358 | 25
3.358 | 4.2
3.3578 | 1
3.3574 | 25
3.3573 | 13
3.3573 | 4.1
3.3568 | 14.7
3.3567 | 17
3.3559 | 5
3.3559 | 6.5
3.3557 | 17
3.3552 | 6.7
3.3548 | 6.5
3.3546 | 8.7
3.3544 | 10.5
3.3544 | 4.4
3.3538 | 8.4
3.3537 | 3
3.353 | 17
3.3526 | 0.7
3.3526 | 12.7
3.3522 | 8.9
3.3522 | 2.5
3.3521 | 8.3
3.3521 | 0
3.3521 | 0
3.3511 | 8.3
3.351 | 3.5
3.3509 | 8
3.3491 | 8.9
3.349 | 2
3.349 | 7.6
3.349 | 4.4
3.349 | 8.8
3.3484 | 9
3.3471 | 10.4
3.3455 | 2
3.3455 | 13.8
3.3454 | 2
3.345 | 7
3.3444 | 5.9
3.3437 | 5.8
3.3436 | 5.7
3.3436 | 4.7
3.3436 | 8.2
3.3432 | 4
3.3432 | 0
3.3431 | 10
3.3428 | 13.4
3.3426 | 10.5
3.3422 | 9.7
3.3418 | 13
3.3415 | 16
3.3413 | 9.8
3.3407 | 10.7
3.3405 | 13
3.3404 | 4
3.3402 | 11.9
3.3399 | 6.8
3.3398 | 10
3.3394 | 4.6
3.3393 | 10.1
3.338 | 3.8
3.338 | 2.15
3.3379 | 16.2
3.3378 | 10
3.3378 | 13.4
3.3377 | 13.3
3.3372 | 10.3
3.3369 | 1.7
3.3356 | 4.3
3.3348 | 2
3.3342 | 11.2
3.3342 | 8.9
3.3333 | 12.6
3.3333 | 3
3.3321 | 10.5
3.332 | 12.5
3.3317 | 3
3.3315 | 1
3.3306 | 11.6
3.33 | 7.5
3.3297 | 2.25
3.3293 | 9.7
3.3293 | 9.6
3.3287 | 3.9
3.3286 | 4.1
3.3281 | 12.1
3.3279 | 7.5
3.3279 | 11.5
3.3269 | 11
3.3268 | 9.5
3.3268 | 5
3.3266 | 8.2
3.3265 | 11.8
3.3261 | 12.3
3.3261 | 6
3.3257 | 8.1
3.3252 | 7
3.325 | 8.5
3.3248 | 10.4
3.3243 | 9
3.324 | 9
3.3238 | 11.5
3.3231 | 0
3.3231 | 13
3.3231 | 10.2
3.3231 | 4.4
3.3222 | 9
3.3217 | 1.2
3.3215 | 8
3.3215 | 0
3.321 | 6
3.3208 | 9.5
3.3203 | 6.3
3.3203 | 26
3.3202 | 1
3.3198 | 20
3.3189 | 7.5
3.3188 | 20.3
3.3182 | 9.2
3.318 | 16
3.318 | 1
3.318 | 9.3
3.318 | 13
3.3173 | 10.5
3.3168 | 5.6
3.3154 | 6
3.3152 | 10.1
3.3152 | 10.9
3.3145 | 9.8
3.3142 | 5
3.314 | 4.3
3.314 | 15.8
3.3138 | 8.6
3.3127 | 5.4
3.3126 | 7.7
3.3117 | 11.1
3.3115 | 3.7
3.311 | 10.5
3.3108 | 9
3.3107 | 9.5
3.3106 | 9
3.3104 | 27
3.3097 | 18
3.309 | 11.1
3.309 | 10
3.3086 | 13.5
3.3084 | 6.5
3.3074 | 10
3.3072 | 1
3.3063 | 1
3.306 | 11.6
3.306 | 7.2
3.3057 | 6.5
3.3052 | 12.5
3.3045 | 19.2
3.3039 | 6.5
3.3024 | 4.8
3.302 | 7.5
3.3013 | 24
3.3012 | 5.6
3.3009 | 1
3.3009 | 7.5
3.3006 | 9.1
3.3005 | 17
3.3005 | 7
3.3004 | 20
3.2999 | 9.5
3.2991 | 11.2
3.2985 | 2
3.2982 | 0
3.2971 | 5.7
3.2971 | 6
3.2969 | 15
3.2962 | 3.2
3.2962 | 7.6
3.2962 | 8.4
3.2961 | 8.9
3.2953 | 9.5
3.2952 | 7.8
3.2947 | 12
3.2943 | 0
3.2941 | 6.8
3.2941 | 9
3.294 | 11
3.294 | 12.7
3.2938 | 11.9
3.2938 | 2.3
3.2933 | 16
3.2931 | 15.9
3.2923 | 10.5
3.2911 | 11.4
3.2902 | 17.5
3.2889 | 8.2
3.2889 | 13.2
3.2882 | 8
3.2882 | 6.7
3.2875 | 9
3.2875 | 21
3.2872 | 28.5
3.287 | 0
3.2868 | 11.5
3.2864 | 9.5
3.2863 | 6.6
3.2858 | 26
3.2856 | 7.8
3.2853 | 11
3.2851 | 9.1
3.2847 | 12
3.2846 | 14
3.2839 | 11.3
3.2838 | 2
3.2838 | 7.8
3.2837 | 11.7
3.2829 | 11.2
3.2828 | 7.5
3.2823 | 8.5
3.282 | 13
3.2817 | 5.8
3.2816 | 0.4
3.2816 | 12.5
3.2816 | 17
3.281 | 13.5
3.2802 | 5.8
3.28 | 10.3
3.2799 | 17.2
3.2795 | 7.4
3.2795 | 15
3.2793 | 18
3.2793 | 5.1
3.2793 | 7.2
3.2784 | 11
3.2784 | 7.6
3.2781 | 5.5
3.278 | 3.6
3.2779 | 6.5
3.2778 | 5.9
3.2774 | 23
3.2765 | 17
3.2762 | 8.9
3.276 | 5.7
3.2758 | 5.8
3.2758 | 9
3.2751 | 3
3.2748 | 9.9
3.2744 | 19
3.2739 | 12.3
3.2738 | 11.2
3.2736 | 17
3.273 | 9.5
3.2729 | 10.5
3.2723 | 17.3
3.2717 | 17.6
3.271 | 11.2
3.2703 | 9
3.2702 | 3.4
3.2697 | 17.7
3.2697 | 2
3.2694 | 11.2
3.2693 | 13
3.2692 | 10.2
3.2688 | 6.7
3.2687 | 6.4
3.2686 | 3
3.2685 | 2
3.2683 | 6
3.2683 | 13.2
3.2683 | 5.5
3.2672 | 0
3.2669 | 4.4
3.2668 | 9.7
3.2663 | 7.9
3.2662 | 9
3.266 | 10.7
3.2659 | 9.5
3.2659 | 11.1
3.2659 | 9
3.2656 | 7.2
3.2656 | 2.3
3.2649 | 11.4
3.2636 | 9.9
3.2625 | 1
3.2622 | 8.9
3.2621 | 9.8
3.2615 | 4.5
3.2613 | 13
3.2603 | 6
3.2595 | 9
3.2595 | 13.4
3.2595 | 6
3.2594 | 7
3.2582 | 9.5
3.258 | 12
3.2576 | 12.9
3.2569 | 7.3
3.2568 | 3.1
3.2562 | 10.6
3.2561 | 9.7
3.2554 | 0
3.2552 | 5
3.2546 | 7.5
3.2534 | 3.5
3.2529 | 1
3.2527 | 10
3.2524 | 21
3.2524 | 11
3.2521 | 7.3
3.252 | 17.5
3.2512 | 12.4
3.2512 | 11
3.2512 | 4
3.2512 | 9.5
3.2503 | 6.9
3.2481 | 6
3.2481 | 2
3.2466 | 12.7
3.246 | 10
3.246 | 0
3.245 | 5
3.2448 | 9.1
3.2448 | 7
3.2444 | 15
3.2442 | 4
3.2442 | 5
3.2441 | 10
3.244 | 2.3
3.244 | 2.2
3.2437 | 11.3
3.2433 | 6.3
3.2433 | 6.9
3.243 | 7.3
3.243 | 7.1
3.2426 | 11.2
3.2423 | 17.4
3.2416 | 3
3.2415 | 4.9
3.2408 | 5
3.2408 | 10.1
3.2406 | 0
3.2398 | 6.2
3.2394 | 7
3.2391 | 3.7
3.2389 | 12.3
3.2388 | 8.7
3.238 | 12.8
3.2379 | 7.5
3.2359 | 13.6
3.2358 | 3
3.2358 | 11.2
3.2352 | 0
3.2352 | 14.8
3.2343 | 1
3.2337 | 8.2
3.2321 | 14
3.232 | 10.5
3.2316 | 5.5
3.2309 | 3.7
3.2309 | 10.5
3.2308 | 7
3.2307 | 0
3.2307 | 13
3.2305 | 17.7
3.2302 | 11.1
3.23 | 11
3.2292 | 7.6
3.2285 | 6
3.2285 | 13.5
3.2281 | 3
3.2278 | 16
3.2276 | 3.3
3.2259 | 11.3
3.2258 | 12.4
3.2239 | 7
3.2237 | 9
3.2237 | 8
3.223 | 7
3.223 | 17
3.2227 | 3.9
3.2218 | 30
3.2212 | 5.2
3.2212 | 8.3
3.2211 | 2
3.2211 | 7.1
3.2208 | 7
3.2204 | 13
3.2202 | 8.9
3.2198 | 4.2
3.2195 | 6.1
3.2195 | 21
3.219 | 9.7
3.218 | 9.2
3.2175 | 5
3.2172 | 0
3.2157 | 5
3.2154 | 11.3
3.2153 | 2.5
3.2153 | 2
3.2149 | 3
3.2145 | 14
3.2145 | 3.9
3.2145 | 9
3.2144 | 8
3.2142 | 5.3
3.214 | 6
3.2123 | 19
3.2113 | 9.7
3.211 | 13
3.2109 | 1.9
3.2104 | 9.9
3.2101 | 11.9
3.2097 | 1
3.2096 | 9.8
3.2094 | 10.4
3.208 | 7
3.2074 | 2
3.2074 | 4.7
3.2072 | 5.8
3.2071 | 0
3.2067 | 7.9
3.2063 | 4.4
3.2063 | 13.5
3.206 | 17.2
3.2058 | 3.4
3.2056 | 11.2
3.2056 | 5.9
3.2054 | 8
3.2053 | 10.2
3.2053 | 0
3.2045 | 7.1
3.2037 | 7.8
3.2033 | 15.5
3.2032 | 8
3.2028 | 9.3
3.2023 | 11
3.2021 | 8
3.2016 | 1
3.201 | 0
3.2007 | 26
3.1999 | 1
3.1999 | 4.5
3.1995 | 12
3.1992 | 4
3.198 | 18
3.1974 | 3.5
3.1971 | 7.2
3.1969 | 8.4
3.1968 | 14.6
3.1965 | 6
3.1965 | 10
3.1958 | 4.5
3.1956 | 7
3.1955 | 5.15
3.1952 | 6.6
3.1949 | 12.5
3.1949 | 5.6
3.1949 | 17
3.1944 | 13.8
3.1943 | 20.3
3.1935 | 12.5
3.193 | 5.6
3.1928 | 0
3.1927 | 7.7
3.1922 | 8.7
3.1921 | 2
3.1921 | 7.1
3.1917 | 10.9
3.1914 | 7.5
3.1914 | 9.7
3.191 | 7.2
3.19 | 25
3.1894 | 8.2
3.1889 | 12.2
3.1885 | 6
3.1885 | 11
3.1882 | 1.15
3.1879 | 7.3
3.1879 | 9.5
3.1878 | 22.06
3.1878 | 11
3.1878 | 4
3.1871 | 3.2
3.1859 | 2
3.1859 | 11.1
3.1854 | 9.7
3.1854 | 5
3.185 | 4.5
3.1849 | 11.9
3.1849 | 10.1
3.1848 | 7.3
3.1843 | 10.5
3.1836 | 6.2
3.1827 | 1
3.1826 | 5
3.1826 | 14.3
3.1824 | 9.7
3.1824 | 13
3.1813 | 10.2
3.1813 | 6
3.181 | 14
3.1808 | 21
3.1808 | 5
3.1805 | 20
3.1804 | 1
3.1804 | 6.2
3.18 | 10.3
3.1797 | 12.8
3.1795 | 6
3.1793 | 1.4
3.1788 | 9.7
3.1786 | 10.1
3.1781 | 11
3.1771 | 9.4
3.1767 | 13
3.1764 | 11.5
3.1762 | 12.7
3.1759 | 11.5
3.1759 | 8.2
3.1753 | 2
3.1753 | 4
3.175 | 8.5
3.1747 | 21
3.1747 | 8.3
3.1747 | 9.5
3.1745 | 5.7
3.1745 | 5.3
3.1741 | 0
3.1741 | 9.5
3.1739 | 12
3.1738 | 24
3.1732 | 15.2
3.1731 | 6.5
3.1729 | 12.7
3.1704 | 9.7
3.1703 | 12.1
3.169 | 16
3.1686 | 9.6
3.1679 | 7
3.1674 | 8
3.1671 | 8.5
3.1664 | 5.9
3.1663 | 4.1
3.1659 | 6.5
3.1652 | 2
3.1646 | 13.5
3.1641 | 23.6
3.1638 | 16.7
3.1636 | 17
3.1632 | 18.7
3.1628 | 6
3.1628 | 9.6
3.1624 | 8
3.1622 | 1.9
3.1622 | 15.4
3.1615 | 0.72
3.1609 | 15.7
3.1607 | 7.5
3.1607 | 9.5
3.1606 | 6.1
3.1604 | 6
3.1594 | 6.6
3.1588 | 6.8
3.1585 | 11.2
3.1581 | 10.5
3.1581 | 10.4
3.1581 | 12.3
3.1581 | 12.1
3.1581 | 3.5
3.158 | 1.6
3.158 | 14
3.1573 | 5.7
3.1568 | 20.3
3.1561 | 2
3.1554 | 2
3.1554 | 7.2
3.1551 | 9
3.1548 | 12.8
3.154 | 8.8
3.1537 | 9
3.1528 | 7
3.1526 | 6.7
3.1521 | 8
3.1517 | 15.9
3.1517 | 10.6
3.1509 | 6
3.1507 | 7
3.1507 | 0
3.1503 | 24
3.1499 | 12.5
3.1498 | 10.5
3.1498 | 7.8
3.1493 | 24
3.1491 | 3.8
3.1491 | 2
3.1481 | 11.5
3.1478 | 7.3
3.1472 | 7.1
3.1471 | 21.7
3.1465 | 6.8
3.1463 | 5
3.1458 | 2
3.1456 | 8
3.1456 | 4.8
3.145 | 12.3
3.145 | 11.3
3.1449 | 1.3
3.1446 | 15.4
3.1444 | 9
3.1437 | 9.5
3.1437 | 7
3.1434 | 3.2
3.1434 | 25
3.143 | 2
3.1428 | 13.2
3.1422 | 9
3.1421 | 17.5
3.1421 | 5
3.1418 | 7
3.1417 | 0
3.1417 | 0
3.1413 | 15.4
3.1411 | 12.5
3.1411 | 14.2
3.1409 | 8
3.1403 | 9.5
3.14 | 4.5
3.1394 | 11
3.1393 | 10.5
3.1391 | 16
3.1391 | 14
3.1389 | 10.8
3.1387 | 7
3.1386 | 10
3.1386 | 18.5
3.1383 | 8.4
3.1382 | 6
3.1378 | 8
3.1377 | 3.3
3.1376 | 7.4
3.1375 | 5.1
3.1368 | 14.1
3.1368 | 9.8
3.1363 | 0
3.1359 | 28
3.1348 | 1.2
3.1336 | 7.3
3.1336 | 10.1
3.133 | 10.8
3.1328 | 9.4
3.1324 | 10
3.1316 | 16
3.1313 | 56
3.1306 | 13.2
3.1302 | 15
3.1295 | 11.7
3.1292 | 8
3.1289 | 8
3.1289 | 13.9
3.1289 | 5.1
3.1289 | 6
3.1282 | 5.4
3.128 | 9.6
3.128 | 7.7
3.1278 | 6
3.1274 | 21
3.1274 | 6.2
3.1273 | 5
3.1264 | 9.8
3.1255 | 3.4
3.1254 | 11.9
3.1245 | 11.2
3.1234 | 10.4
3.123 | 4.9
3.123 | 12.5
3.1227 | 10.6
3.1222 | 7
3.1217 | 7.2
3.1213 | 10.9
3.1212 | 10.1
3.1193 | 0
3.1193 | 12
3.1191 | 10.1
3.1189 | 10.2
3.1187 | 7.4
3.1164 | 16.3
3.1157 | 8.5
3.1156 | 3.5
3.115 | 2
3.115 | 15.2
3.115 | 2
3.1143 | 11.1
3.1143 | 6
3.1143 | 14.6
3.1143 | 11.8
3.1143 | 3
3.114 | 8.7
3.1136 | 13.8
3.1134 | 10.4
3.1129 | 8.7
3.1121 | 14
3.1117 | 8.5
3.1116 | 5.3
3.1104 | 18
3.1104 | 14.2
3.11 | 13.4
3.1091 | 6.2
3.109 | 10.5
3.1085 | 8.3
3.108 | 4.4
3.108 | 7.2
3.1076 | 5.1
3.1075 | 2
3.1071 | 6.6
3.1071 | 7.7
3.1059 | 11.5
3.1056 | 12.3
3.1055 | 8.1
3.1046 | 12.5
3.1034 | 15
3.1033 | 5.2
3.1025 | 2.6
3.1021 | 12
3.1021 | 8.2
3.102 | 7.5
3.102 | 0
3.1019 | 8.5
3.1019 | 16.6
3.1009 | 2
3.1009 | 16.9
3.1006 | 17.9
3.0999 | 4.2
3.0998 | 9.8
3.0997 | 2.35
3.0992 | 5.3
3.0986 | 3.6
3.0985 | 6.5
3.098 | 7.5
3.0969 | 11.65
3.0964 | 9.5
3.0938 | 8.9
3.0938 | 18
3.0935 | 7.6
3.0932 | 5.2
3.0929 | 24
3.0918 | 5.4
3.0918 | 6.6
3.0917 | 2
3.0902 | 10.5
3.0895 | 7
3.0886 | 0
3.0886 | 3.3
3.0878 | 6.5
3.0876 | 12.9
3.0874 | 13
3.0874 | 7.5
3.087 | 6
3.0867 | 23
3.0861 | 5.7
3.0859 | 6
3.0845 | 6
3.0844 | 8
3.083 | 11.8
3.0823 | 11
3.0822 | 0
3.0816 | 0
3.0816 | 5.8
3.0816 | 14.6
3.0816 | 5
3.0809 | 24
3.0805 | 6
3.0805 | 3
3.0805 | 8.5
3.0804 | 0
3.0797 | 8.5
3.0797 | 16
3.0797 | 2
3.0793 | 5.7
3.0792 | 8.6
3.0783 | 9.1
3.078 | 17.3
3.0777 | 13.2
3.0775 | 8.2
3.0772 | 11.5
3.0769 | 14
3.0764 | 7
3.0764 | 8.5
3.0763 | 3.4
3.0763 | 2
3.0763 | 18.2
3.0761 | 5
3.076 | 24
3.076 | 7.6
3.076 | 6
3.0757 | 8.2
3.0755 | 2
3.0733 | 1
3.0733 | 9
3.0733 | 12.7
3.0733 | 4.9
3.0732 | 14.5
3.0731 | 9
3.0728 | 2
3.0728 | 1
3.0726 | 11.7
3.0722 | 4.6
3.0722 | 4.5
3.0714 | 5.5
3.0714 | 5.5
3.0713 | 1
3.071 | 10.5
3.071 | 10.7
3.0709 | 2
3.0707 | 2
3.0705 | 8.8
3.0699 | 6.4
3.0698 | 9.7
3.0692 | 10.7
3.0691 | 12.9
3.0682 | 18
3.0673 | 12.5
3.0665 | 5.5
3.0664 | 7.9
3.0663 | 14
3.0661 | 12
3.0661 | 1
3.0661 | 10.5
3.065 | 8
3.0649 | 10
3.0647 | 19.2
3.0642 | 2
3.0641 | 3.3
3.0641 | 3.3
3.0641 | 12
3.0641 | 8.8
3.0637 | 9.3
3.0637 | 4.1
3.0634 | 1
3.0634 | 5
3.0633 | 11
3.063 | 12.7
3.0626 | 26
3.0622 | 13.6
3.062 | 11.3
3.062 | 6.3
3.062 | 6
3.062 | 15
3.0619 | 6
3.0611 | 14
3.0608 | 17
3.0605 | 0
3.0601 | 10.3
3.06 | 0
3.0598 | 0
3.0595 | 7
3.0592 | 5.9
3.059 | 24
3.0583 | 13.5
3.0581 | 12.3
3.0577 | 8.1
3.0577 | 9.9
3.0577 | 8.3
3.0567 | 4
3.0561 | 6.6
3.0561 | 8.2
3.0559 | 11
3.0557 | 5
3.0557 | 13
3.0549 | 9
3.0549 | 11.5
3.0546 | 2
3.0542 | 9.5
3.0541 | 10
3.0535 | 7
3.0531 | 13.2
3.0529 | 9
3.0527 | 11
3.0527 | 8
3.0525 | 6.5
3.0518 | 2.7
3.0517 | 12.9
3.0516 | 3
3.051 | 9
3.051 | 8
3.0503 | 5.9
3.0487 | 3.9
3.0486 | 6
3.0485 | 13
3.048 | 4
3.048 | 18.5
3.0474 | 7.3
3.0466 | 7.5
3.0463 | 9.1
3.0459 | 1.2
3.0458 | 12
3.0452 | 18
3.0447 | 14
3.0445 | 18
3.0438 | 5.3
3.0438 | 7.5
3.0436 | 2
3.0424 | 4.5
3.0418 | 12
3.0416 | 8
3.0416 | 23
3.0409 | 24
3.0409 | 11
3.0406 | 5.2
3.0404 | 6
3.0404 | 3.4
3.0401 | 17.3
3.0401 | 16
3.0394 | 14.5
3.039 | 15.5
3.0387 | 8.8
3.0383 | 11
3.0383 | 11.8
3.0374 | 7.1
3.0371 | 5.2
3.0356 | 5
3.0356 | 7.3
3.0349 | 7.2
3.0346 | 10.5
3.0346 | 4
3.0346 | 2
3.0346 | 8
3.0346 | 8.9
3.0343 | 23
3.0342 | 9.3
3.0339 | 21
3.0339 | 7.6
3.0331 | 5.5
3.0326 | 8.5
3.0322 | 12.8
3.0314 | 0
3.0312 | 10.6
3.0304 | 14
3.0302 | 7.2
3.0302 | 7
3.0301 | 7.9
3.0299 | 9.3
3.0296 | 9.2
3.0284 | 5.8
3.0281 | 7
3.0274 | 4.3
3.0273 | 10.1
3.0272 | 7.1
3.0268 | 11
3.0268 | 11.4
3.0264 | 10.4
3.026 | 17
3.026 | 2
3.0256 | 4.5
3.0256 | 9
3.0253 | 4
3.0253 | 7.6
3.0253 | 13.6
3.0248 | 2.9
3.0247 | 8.5
3.0245 | 6.5
3.0245 | 11.5
3.0238 | 2
3.0232 | 10.3
3.0232 | 3.6
3.0232 | 10.9
3.0232 | 4
3.0227 | 26
3.0225 | 6.4
3.0219 | 10.6
3.0219 | 3.5
3.0211 | 4
3.0211 | 9
3.0205 | 12.5
3.0199 | 7
3.0199 | 7.1
3.0198 | 8
3.0198 | 14
3.0196 | 21.2
3.0195 | 6
3.0191 | 6
3.0191 | 5.7
3.019 | 5
3.019 | 11.5
3.0185 | 4.5
3.0167 | 6
3.0158 | 8.4
3.0154 | 13.5
3.015 | 2.9
3.015 | 3
3.0149 | 9.8
3.0144 | 5
3.0138 | 3
3.0135 | 31
3.0135 | 7.9
3.0123 | 16.3
3.0119 | 12
3.0117 | 7.9
3.0113 | 12
3.011 | 9
3.011 | 5.6
3.011 | 7.5
3.0109 | 2
3.0109 | 7.4
3.0103 | 7
3.0102 | 5.6
3.0102 | 13
3.0097 | 5.8
3.0097 | 5.9
3.0089 | 15
3.0088 | 4.9
3.0088 | 10.5
3.0084 | 12
3.0081 | 10.8
3.0074 | 6.3
3.0071 | 9
3.0067 | 10.4
3.0064 | 10.4
3.0064 | 11.3
3.0063 | 9.3
3.006 | 7.3
3.0056 | 13.5
3.0056 | 6
3.0053 | 10.6
3.0053 | 16
3.0052 | 7
3.0049 | 13.1
3.0048 | 14
3.0043 | 9.4
3.0038 | 7.5
3.0036 | 11
3.0036 | 5.7
3.0035 | 9.5
3.0034 | 7.4
3.003 | 2
3.0027 | 9.4
3.0022 | 12
3.0017 | 4.8
3.0017 | 12.4
3.0015 | 30
3.0012 | 11.7
3.0011 | 7
3.001 | 8.5
3.0008 | 9.6
2.9994 | 8
2.9986 | 10
2.9979 | 8.5
2.9975 | 7
2.9975 | 3.6
2.9973 | 8.3
2.9973 | 9.5
2.9962 | 7
2.9959 | 6.4
2.9956 | 15
2.9951 | 10.2
2.9946 | 5.4
2.9946 | 2
2.9943 | 9.1
2.9941 | 8
2.9937 | 2.6
2.9937 | 2
2.9937 | 8
2.9935 | 10
2.9928 | 9
2.9928 | 9.4
2.9911 | 12
2.9908 | 7
2.9907 | 10.3
2.9905 | 9
2.9902 | 4.5
2.9898 | 9.7
2.9891 | 7
2.989 | 10.5
2.9888 | 14
2.9877 | 2.5
2.9876 | 8
2.9874 | 7
2.9874 | 11.5
2.9874 | 15
2.9854 | 11.5
2.9853 | 10.6
2.9842 | 8
2.984 | 2
2.984 | 2
2.9831 | 7.2
2.9823 | 9.2
2.9823 | 9
2.9818 | 23.6
2.9811 | 11
2.9811 | 16
2.981 | 7.2
2.9803 | 4.1
2.979 | 7
2.9788 | 1
2.9784 | 7
2.9782 | 9.8
2.9782 | 3
2.9775 | 6
2.9774 | 2
2.9771 | 6.5
2.9769 | 15.6
2.9768 | 6
2.9767 | 3
2.9767 | 6.5
2.9762 | 14
2.9751 | 7.4
2.9747 | 9.5
2.9734 | 4
2.973 | 6
2.9726 | 15.3
2.9725 | 2
2.9718 | 7.7
2.9717 | 9.8
2.9709 | 8.7
2.97 | 18
2.9699 | 2
2.9697 | 17
2.9697 | 5.8
2.969 | 7
2.9688 | 5.5
2.9679 | 7.5
2.9674 | 20
2.9674 | 17
2.9673 | 9.2
2.967 | 5.9
2.967 | 7
2.9666 | 5.8
2.9659 | 3.3
2.9659 | 9.1
2.9658 | 8
2.9651 | 5.5
2.9651 | 11.7
2.9642 | 6.5
2.9639 | 6.2
2.9637 | 2
2.9637 | 5.2
2.9634 | 10
2.9629 | 7.4
2.9621 | 3.1
2.961 | 2
2.9607 | 9.8
2.9605 | 4
2.9603 | 5.7
2.9592 | 13
2.9587 | 8.3
2.9587 | 10
2.9587 | 12
2.9585 | 9.7
2.9581 | 11
2.9579 | 9.7
2.9576 | 11.2
2.9569 | 11.2
2.9569 | 2
2.9569 | 13.8
2.9569 | 4.1
2.9564 | 13
2.9558 | 6.5
2.9549 | 4
2.9543 | 10.2
2.9543 | 23
2.9541 | 8.1
2.9541 | 4.5
2.9522 | 6.5
2.9516 | 8
2.9516 | 9.8
2.9509 | 6
2.9508 | 4.8
2.9508 | 4.1
2.9506 | 10
2.9506 | 12.1
2.9499 | 16.3
2.9496 | 21.6
2.9488 | 4.4
2.9486 | 18
2.948 | 19.3
2.9479 | 15.1
2.947 | 1
2.9447 | 2
2.9447 | 2
2.9447 | 8
2.9444 | 7
2.943 | 6.2
2.943 | 10.4
2.9419 | 9.5
2.9418 | 3.6
2.9416 | 17.3
2.9416 | 19.5
2.9414 | 0
2.941 | 17.1
2.9406 | 11
2.9394 | 10.5
2.9391 | 17
2.9389 | 3
2.9389 | 8.4
2.9376 | 10.9
2.9374 | 10
2.9373 | 6
2.9373 | 11
2.9373 | 10
2.9372 | 9.3
2.9368 | 3.6
2.9365 | 4.9
2.9363 | 16
2.9363 | 4.8
2.9359 | 12
2.9346 | 9
2.9346 | 21
2.9345 | 4.2
2.9339 | 10.9
2.9338 | 2
2.9336 | 21
2.9336 | 11.1
2.9325 | 9.5
2.9316 | 8.4
2.9313 | 10.3
2.9303 | 8.2
2.9302 | 4.5
2.93 | 4
2.9295 | 10.6
2.9295 | 4.7
2.9291 | 2.7
2.9283 | 2
2.9282 | 6.4
2.9281 | 10
2.9275 | 5
2.9275 | 5.8
2.9268 | 2
2.9265 | 11
2.9265 | 6
2.9265 | 9
2.9262 | 5.5
2.9261 | 12.7
2.9259 | 7.8
2.9248 | 5.7
2.9247 | 1
2.9242 | 5.6
2.9241 | 12.4
2.9236 | 2
2.9228 | 8.6
2.9227 | 10
2.9222 | 7.5
2.922 | 9.4
2.9215 | 18
2.9205 | 6
2.92 | 9
2.9199 | 6.5
2.9199 | 4.6
2.9194 | 6.5
2.9193 | 7.8
2.9189 | 12
2.9189 | 8.8
2.9185 | 3
2.9172 | 18
2.9172 | 9.5
2.9167 | 4.5
2.9165 | 10.5
2.9163 | 5.5
2.9163 | 9.9
2.9161 | 22.3
2.9161 | 4.4
2.9161 | 10.7
2.9135 | 9.2
2.9134 | 10.4
2.9134 | 12.4
2.913 | 3.7
2.9124 | 5.8
2.9121 | 4.5
2.9111 | 5.9
2.9091 | 16
2.909 | 2
2.909 | 13.4
2.909 | 17
2.909 | 11.5
2.9086 | 10.6
2.9079 | 8
2.9071 | 15
2.9069 | 4.8
2.9064 | 23
2.9063 | 6.5
2.9054 | 9.4
2.9054 | 7.8
2.9046 | 11
2.9046 | 14.8
2.9021 | 5.6
2.9021 | 8.2
2.9017 | 5.3
2.9014 | 8.7
2.9012 | 14
2.9007 | 13.6
2.9001 | 4.5
2.8999 | 3.6
2.8994 | 3
2.8981 | 8.9
2.8959 | 7.6
2.8959 | 2
2.8952 | 10
2.8943 | 10.4
2.8943 | 9.9
2.8943 | 18.8
2.8939 | 6.7
2.8932 | 7.5
2.893 | 6
2.8915 | 8.2
2.8908 | 11
2.8907 | 6.7
2.8895 | 9
2.8891 | 11
2.8891 | 10.9
2.8888 | 23
2.8887 | 0
2.8885 | 18.7
2.8883 | 4
2.8883 | 6
2.8883 | 15.8
2.8871 | 12.5
2.8871 | 7.6
2.8864 | 10
2.8864 | 14
2.8861 | 16
2.8857 | 8.4
2.885 | 5.2
2.8849 | 10.3
2.8839 | 19.4
2.8836 | 8.2
2.8831 | 9
2.8828 | 7
2.8826 | 5.4
2.8824 | 17.3
2.8816 | 1.2
2.8816 | 14
2.8816 | 7.7
2.8811 | 14
2.8802 | 11.75
2.8797 | 9.6
2.8797 | 9.5
2.879 | 8
2.8783 | 9.5
2.8768 | 7.5
2.8768 | 9.5
2.8763 | 1.85
2.8763 | 18.2
2.8762 | 14.7
2.8761 | 5
2.876 | 9
2.8757 | 15.7
2.8744 | 6.7
2.8738 | 5.7
2.8733 | 13
2.8728 | 12
2.8727 | 8.1
2.8719 | 14.9
2.8713 | 1.2
2.8713 | 10.5
2.8712 | 17
2.8712 | 11
2.8685 | 8
2.8684 | 8.6
2.8682 | 6.6
2.8677 | 25
2.867 | 9.8
2.867 | 5.5
2.867 | 9.9
2.8662 | 15.2
2.8657 | 9.5
2.8656 | 7.6
2.8656 | 10
2.8656 | 7.8
2.8655 | 12.2
2.8653 | 12
2.8635 | 8.5
2.8631 | 5.8
2.8629 | 8
2.8629 | 7
2.8622 | 21.2
2.8617 | 8.7
2.8617 | 9.5
2.8617 | 12
2.861 | 8.8
2.8604 | 6.8
2.8596 | 6
2.8595 | 4
2.8594 | 6
2.859 | 12.7
2.859 | 10.4
2.8586 | 14
2.8582 | 10
2.858 | 6.2
2.8577 | 5.7
2.8561 | 3
2.8546 | 9
2.8544 | 3.8
2.8528 | 2
2.8528 | 4
2.8516 | 10.5
2.8516 | 12.9
2.8515 | 4.4
2.8503 | 6.4
2.8501 | 21
2.8501 | 1
2.8498 | 6.2
2.8498 | 10.6
2.8496 | 6
2.8494 | 7.9
2.8494 | 4
2.8494 | 14
2.8482 | 8.5
2.8473 | 11.1
2.847 | 7
2.8452 | 6
2.8444 | 7
2.8441 | 10
2.8435 | 3
2.8435 | 6.8
2.8435 | 10.7
2.8433 | 4.5
2.8431 | 10
2.8428 | 9
2.8413 | 5.3
2.8411 | 9
2.8408 | 22.6
2.8403 | 13.5
2.8401 | 9
2.84 | 6.7
2.8389 | 9
2.8384 | 2
2.8379 | 0.4
2.8379 | 8.9
2.8379 | 9.3
2.8379 | 10
2.8378 | 6
2.8378 | 0
2.8376 | 5.6
2.8375 | 11.1
2.8364 | 18.5
2.8355 | 1
2.835 | 5.4
2.835 | 16
2.8348 | 9.8
2.8346 | 8.2
2.834 | 7.9
2.8333 | 3
2.8332 | 8
2.8327 | 8.2
2.8325 | 9.5
2.8319 | 2.3
2.8316 | 10.2
2.8307 | 20
2.8303 | 8.6
2.8297 | 11.2
2.829 | 9.6
2.8285 | 9.3
2.8284 | 13.4
2.8277 | 10.6
2.8277 | 7.6
2.8267 | 8.9
2.8266 | 4.3
2.8261 | 5.8
2.826 | 16
2.8256 | 20.2
2.8255 | 7.5
2.8255 | 9.3
2.8253 | 17
2.8245 | 5.4
2.8241 | 6
2.8233 | 14
2.8231 | 7
2.8226 | 7.5
2.822 | 8.4
2.8202 | 6.3
2.8202 | 5.9
2.8192 | 3
2.8187 | 5
2.8185 | 22
2.8182 | 9
2.8182 | 16
2.8179 | 5.1
2.8178 | 8
2.8167 | 9.8
2.8164 | 10.7
2.8164 | 10.5
2.8161 | 13.8
2.8161 | 16
2.8155 | 7.9
2.8153 | 17.8
2.8147 | 4.1
2.8144 | 11
2.8144 | 9.3
2.8126 | 10.3
2.8124 | 3.5
2.8122 | 4.9
2.8117 | 14.2
2.8115 | 13
2.8114 | 8.5
2.8108 | 14.8
2.8104 | 11
2.8083 | 15
2.8083 | 2.2
2.8076 | 11.5
2.8066 | 4.6
2.8063 | 4.7
2.8057 | 2
2.8056 | 8
2.8051 | 7.9
2.8047 | 10
2.8045 | 9.6
2.8036 | 3.4
2.8027 | 8.4
2.8022 | 1.8
2.8016 | 9.6
2.8015 | 12
2.8015 | 16
2.8009 | 12
2.7983 | 6.3
2.7973 | 11.5
2.7967 | 10.2
2.7955 | 5
2.7953 | 26
2.7953 | 12.3
2.7942 | 10.5
2.7942 | 5.8
2.794 | 8.1
2.794 | 9.1
2.7938 | 16.6
2.7938 | 5
2.7926 | 9
2.7922 | 8.5
2.7922 | 12
2.7918 | 23
2.7897 | 5.5
2.7892 | 7.7
2.7883 | 7
2.7883 | 6
2.7882 | 7
2.7881 | 2
2.7878 | 8
2.7875 | 6.3
2.787 | 3
2.787 | 8.6
2.7869 | 18
2.7864 | 10
2.7854 | 8
2.7849 | 8.5
2.7847 | 7.6
2.7844 | 6.4
2.7843 | 8
2.7826 | 9.9
2.7816 | 6.1
2.7814 | 7.9
2.781 | 9.3
2.7809 | 7.3
2.7807 | 6.9
2.7787 | 18
2.778 | 4.3
2.7777 | 7.4
2.7777 | 8
2.777 | 5.4
2.7768 | 14.95
2.7756 | 12.5
2.7751 | 15
2.7746 | 9
2.7744 | 21
2.7744 | 6.4
2.7739 | 10.8
2.7734 | 8.9
2.7731 | 21
2.7728 | 10.5
2.7728 | 10.7
2.7725 | 6.4
2.7722 | 3.2
2.7721 | 1.2
2.772 | 12.5
2.7714 | 11.2
2.7713 | 12.2
2.7707 | 3.5
2.7692 | 24
2.7689 | 10
2.7686 | 7.5
2.7686 | 11.3
2.7685 | 10.5
2.7671 | 14.4
2.7671 | 21
2.7671 | 11
2.7664 | 10
2.7656 | 4.5
2.7653 | 5.5
2.7652 | 2
2.7646 | 2.7
2.7632 | 5.3
2.7632 | 5
2.7627 | 5.4
2.7622 | 2
2.7622 | 9.7
2.762 | 5.2
2.7615 | 18.4
2.7601 | 13.2
2.7601 | 11
2.7598 | 7
2.7598 | 4.3
2.7598 | 6.45
2.7594 | 12
2.7588 | 10.5
2.7586 | 25
2.7584 | 17.8
2.7584 | 12.5
2.7584 | 14
2.7581 | 7
2.7581 | 8.9
2.758 | 0.3
2.7579 | 19
2.7578 | 5.4
2.7574 | 5.5
2.7561 | 1
2.7561 | 9.7
2.7548 | 24.5
2.7525 | 14
2.7525 | 8
2.7522 | 6.8
2.7516 | 9.5
2.751 | 9.6
2.7483 | 5
2.7474 | 10
2.7461 | 4
2.7453 | 6
2.7453 | 7.5
2.7451 | 7
2.7447 | 9.7
2.7439 | 3.4
2.7439 | 8.6
2.7439 | 13
2.7438 | 6.8
2.7418 | 7.1
2.7411 | 11
2.7411 | 29
2.7404 | 7.9
2.739 | 7.6
2.7385 | 9.5
2.7383 | 11
2.7383 | 9
2.738 | 7.7
2.738 | 13
2.7372 | 6.4
2.7367 | 7
2.7367 | 10.4
2.7355 | 6
2.7343 | 5.9
2.7331 | 9.5
2.7329 | 5.2
2.732 | 8
2.7317 | 26
2.7317 | 7.7
2.7314 | 9.8
2.7312 | 6.8
2.7305 | 16.7
2.7305 | 17
2.7305 | 12
2.7295 | 7.7
2.7295 | 4.9
2.7295 | 5
2.7295 | 6.8
2.7287 | 6
2.7282 | 11.6
2.728 | 13.2
2.728 | 6.8
2.7276 | 7.7
2.7276 | 11.2
2.7271 | 5.8
2.727 | 9.7
2.7263 | 12
2.7261 | 5.2
2.7261 | 18
2.7259 | 26
2.7249 | 16.2
2.7249 | 15
2.7242 | 10.4
2.7234 | 11.3
2.7231 | 5.8
2.7224 | 12.8
2.7222 | 10.5
2.722 | 19
2.722 | 10.7
2.7216 | 6.5
2.7215 | 5.7
2.7215 | 6.2
2.7202 | 12
2.7198 | 4
2.7198 | 15
2.7191 | 12.3
2.7188 | 10
2.7181 | 9
2.7179 | 13
2.7179 | 7.6
2.7168 | 6.5
2.7165 | 9.9
2.7165 | 22.5
2.7161 | 19.5
2.7161 | 8
2.7161 | 9
2.7156 | 8
2.7152 | 7
2.7151 | 5
2.7147 | 18
2.712 | 19
2.7107 | 8
2.7099 | 10.1
2.7088 | 5.4
2.7084 | 15.2
2.7074 | 6
2.7067 | 4.9
2.7052 | 0
2.7052 | 8.9
2.7051 | 10.1
2.7045 | 9.6
2.7038 | 6
2.7038 | 12.4
2.7033 | 3
2.7033 | 6.1
2.7031 | 11.5
2.7016 | 6.5
2.7016 | 13.8
2.7002 | 11
2.7001 | 2
2.6997 | 5.6
2.6985 | 7.5
2.6979 | 5
2.6979 | 3
2.6973 | 11
2.6968 | 8.3
2.6968 | 9
2.6968 | 11
2.6965 | 8
2.696 | 9.7
2.6959 | 11
2.6953 | 14.5
2.695 | 12
2.6944 | 10.6
2.6943 | 9
2.6934 | 3.5
2.6931 | 1
2.6913 | 7
2.6912 | 4.1
2.6911 | 10.2
2.6908 | 15
2.6908 | 6.2
2.6907 | 5.8
2.6905 | 12.1
2.6902 | 1
2.6901 | 12
2.6899 | 9
2.6897 | 7
2.6895 | 3
2.689 | 10.2
2.6888 | 3
2.6879 | 6
2.6875 | 6.7
2.6873 | 9.6
2.6872 | 10.2
2.6865 | 23.7
2.6865 | 13.1
2.6862 | 5.2
2.6858 | 10.5
2.6838 | 14.2
2.6837 | 10.1
2.6834 | 2.9
2.6834 | 22
2.683 | 25.5
2.6829 | 7.5
2.6829 | 20.3
2.6827 | 20
2.6822 | 4.7
2.682 | 11
2.6817 | 7.2
2.6816 | 18.5
2.6813 | 11.4
2.6813 | 9.5
2.681 | 3.5
2.6806 | 12.3
2.6797 | 8
2.6792 | 7.5
2.6792 | 12
2.679 | 9
2.6786 | 26.3
2.6778 | 10.9
2.6778 | 21.5
2.6771 | 6
2.6771 | 8
2.6764 | 14.4
2.6762 | 2
2.6761 | 13
2.6757 | 5
2.675 | 12
2.675 | 11
2.6749 | 10.5
2.6748 | 2
2.6742 | 14.1
2.6737 | 6
2.6735 | 26
2.6728 | 5.7
2.6722 | 12.8
2.6722 | 10
2.6721 | 14
2.6721 | 7.3
2.6714 | 14.2
2.6714 | 12
2.6703 | 13.2
2.6699 | 13.4
2.6688 | 10
2.6679 | 2
2.6677 | 7.6
2.6674 | 13.5
2.6669 | 15
2.6666 | 10.8
2.666 | 12
2.6652 | 10.2
2.6651 | 20.7
2.6651 | 21.5
2.6651 | 17
2.6649 | 14.6
2.6644 | 15
2.6643 | 9.1
2.664 | 17
2.6639 | 10.8
2.6637 | 19.2
2.6637 | 17.5
2.6637 | 3.8
2.6633 | 9
2.6633 | 13
2.663 | 3.25
2.6629 | 14.8
2.6623 | 10.4
2.6618 | 25
2.6615 | 4
2.6614 | 10
2.6614 | 11
2.6602 | 4.8
2.6594 | 11.5
2.6588 | 18.7
2.6579 | 21
2.6579 | 20.6
2.6579 | 11
2.6578 | 1
2.6574 | 11.9
2.6572 | 6.6
2.6572 | 5.3
2.6572 | 7
2.6568 | 7
2.656 | 25
2.6553 | 9.8
2.6553 | 12.7
2.6546 | 10
2.6545 | 26
2.6545 | 19.1
2.6545 | 9.9
2.6545 | 10.2
2.6543 | 15.1
2.6543 | 3.8
2.6538 | 11.7
2.6531 | 11.2
2.6531 | 8.3
2.6528 | 15
2.6523 | 3.6
2.6515 | 9
2.6508 | 1
2.6506 | 7
2.6492 | 14.5
2.6489 | 7
2.6489 | 5.2
2.6489 | 11.4
2.6475 | 9.7
2.6475 | 0
2.6474 | 10
2.6468 | 5.9
2.6467 | 6
2.6463 | 5.6
2.6461 | 15.3
2.6455 | 66
2.6454 | 26.5
2.6436 | 12.5
2.6433 | 6.8
2.6426 | 2
2.6426 | 11.1
2.6419 | 16
2.6415 | 10.4
2.6405 | 12.6
2.6401 | 6.2
2.64 | 10
2.64 | 14
2.6398 | 16.4
2.6398 | 5.2
2.6398 | 17
2.6391 | 6
2.6386 | 0
2.6385 | 7
2.6384 | 10
2.6378 | 6
2.6371 | 15.5
2.637 | 24
2.6362 | 9.9
2.6362 | 11.8
2.6361 | 4.2
2.6354 | 8.8
2.6353 | 10
2.6352 | 12
2.6352 | 4.6
2.6342 | 13
2.634 | 12.3
2.6339 | 8.5
2.6338 | 1
2.6338 | 9
2.6335 | 10.8
2.6327 | 7.8
2.6319 | 13
2.6318 | 1.5
2.6317 | 8
2.6313 | 15.6
2.6307 | 7.7
2.6299 | 9.1
2.6298 | 14.6
2.6297 | 5.9
2.6293 | 13
2.6293 | 12
2.6292 | 8.7
2.6292 | 5.5
2.6288 | 11.8
2.6288 | 8.9
2.6288 | 10.1
2.6287 | 6.6
2.6285 | 8.2
2.6278 | 10.7
2.6272 | 4
2.6266 | 2.9
2.6265 | 8.9
2.6264 | 13.2
2.6263 | 4.5
2.6252 | 4.5
2.6247 | 14.6
2.6245 | 18.4
2.6229 | 3.7
2.6228 | 6
2.6226 | 26
2.6223 | 13
2.6215 | 12.4
2.6215 | 15.1
2.6211 | 18.1
2.6207 | 16
2.6194 | 11.8
2.6193 | 3.7
2.6187 | 10.5
2.6179 | 0
2.6179 | 2.9
2.6178 | 13.5
2.6175 | 3.5
2.6171 | 12
2.6171 | 4.1
2.6167 | 10.7
2.6164 | 16
2.6146 | 13.3
2.6146 | 5.6
2.6142 | 13.5
2.6142 | 8
2.6138 | 4.2
2.6135 | 4.6
2.6135 | 10.1
2.6131 | 21
2.6124 | 10
2.6113 | 11.5
2.6106 | 4
2.6106 | 4.6
2.6106 | 8.9
2.6102 | 1
2.6102 | 5.5
2.6099 | 10.5
2.6084 | 6
2.6078 | 4
2.6078 | 9
2.6078 | 13
2.6078 | 4.4
2.6073 | 7.8
2.607 | 12.3
2.607 | 8.4
2.607 | 11.4
2.6062 | 7
2.6053 | 12
2.6051 | 7.4
2.6049 | 9.5
2.6044 | 10.3
2.6043 | 19
2.6037 | 19.2
2.6033 | 4
2.6033 | 9
2.6033 | 8.9
2.6033 | 4.4
2.6028 | 10
2.6018 | 12
2.6015 | 15.2
2.6012 | 9.5
2.601 | 7.7
2.601 | 18.3
2.6007 | 13.1
2.6006 | 5
2.5997 | 11
2.5996 | 15
2.5989 | 11
2.5989 | 6.7
2.5985 | 4.7
2.5981 | 4.4
2.5978 | 15
2.5976 | 10.8
2.5976 | 10.5
2.5975 | 10.5
2.5968 | 16.7
2.5964 | 19
2.5955 | 6
2.5947 | 5
2.5947 | 11.2
2.594 | 3
2.5935 | 26
2.5934 | 5
2.5934 | 10.5
2.5924 | 10.3
2.5924 | 10.7
2.5921 | 6
2.5921 | 15
2.5917 | 2
2.5913 | 25
2.5902 | 16.2
2.5899 | 10.4
2.5895 | 6.2
2.5886 | 6.5
2.5884 | 8.3
2.5882 | 2
2.5873 | 15
2.587 | 13.5
2.5868 | 5.2
2.5868 | 7
2.5863 | 8.3
2.5863 | 17.8
2.5863 | 3
2.5859 | 9
2.5851 | 11.8
2.5844 | 11.2
2.5833 | 5.5
2.5827 | 21
2.5818 | 14.5
2.5815 | 8
2.5815 | 8.9
2.5814 | 21
2.58 | 7.5
2.5797 | 11
2.5793 | 13
2.5792 | 17.6
2.5785 | 11.5
2.5779 | 11.3
2.5771 | 5
2.5771 | 8.9
2.5771 | 5
2.5771 | 20
2.5771 | 6
2.5771 | 2
2.5764 | 8.3
2.5764 | 9
2.576 | 12.9
2.5749 | 3.8
2.5745 | 13
2.5743 | 13.5
2.5742 | 1.9
2.5726 | 6
2.5724 | 14
2.5706 | 9.6
2.5705 | 6.7
2.5705 | 7.6
2.5701 | 13.7
2.5701 | 18
2.57 | 10.5
2.57 | 13.2
2.5699 | 9
2.5693 | 13.5
2.5691 | 18.5
2.5687 | 20.6
2.5687 | 11.5
2.5687 | 13.3
2.5687 | 6.3
2.5686 | 9
2.5669 | 0
2.5666 | 24
2.5666 | 6
2.5654 | 4.1
2.5652 | 4.5
2.5651 | 9.7
2.5648 | 11.1
2.5644 | 2
2.564 | 13
2.5633 | 1.5
2.5633 | 14.5
2.5633 | 10
2.5633 | 10
2.5633 | 10.6
2.5633 | 10.4
2.5633 | 12.7
2.5633 | 10.6
2.5633 | 7.5
2.5633 | 19.5
2.5631 | 8.4
2.5626 | 3.8
2.5626 | 8
2.5624 | 11.2
2.5624 | 11
2.5614 | 2
2.5613 | 6.9
2.5601 | 9
2.5599 | 21
2.5594 | 6.4
2.5592 | 10
2.5592 | 12.7
2.5589 | 11.5
2.5588 | 11.7
2.5588 | 10
2.5585 | 0
2.5576 | 3
2.5576 | 9
2.5576 | 9.8
2.5574 | 10.3
2.5572 | 16.4
2.5571 | 5
2.5565 | 3.9
2.556 | 4.6
2.556 | 20
2.5559 | 7.1
2.5553 | 6.5
2.5546 | 10.5
2.5546 | 2
2.5542 | 17
2.5542 | 22.4
2.554 | 25
2.5538 | 3
2.5532 | 4.5
2.5518 | 11
2.5517 | 11.5
2.5511 | 7.5
2.5505 | 18.5
2.5505 | 12
2.5498 | 26
2.5495 | 13
2.549 | 9.1
2.549 | 13
2.5484 | 10.8
2.5483 | 1
2.548 | 0
2.5476 | 1
2.5476 | 9.9
2.5476 | 11.2
2.5473 | 6
2.547 | 1
2.5469 | 17
2.5469 | 5.4
2.5469 | 16
2.5469 | 15.5
2.5455 | 15
2.5455 | 14.4
2.5455 | 14.4
2.5455 | 7.8
2.5451 | 0
2.5451 | 0
2.5447 | 1
2.5447 | 12.6
2.5444 | 14.3
2.5428 | 7
2.5425 | 1
2.5419 | 21
2.5419 | 6
2.5415 | 9.3
2.5413 | 14
2.5413 | 9.9
2.5408 | 18.1
2.5404 | 4.5
2.54 | 6
2.54 | 10.9
2.5399 | 8.3
2.5397 | 6.2
2.538 | 1
2.5374 | 1
2.5371 | 2
2.537 | 10.1
2.5365 | 16
2.5363 | 22
2.5363 | 10
2.5363 | 11.2
2.5361 | 4.2
2.5361 | 11
2.5361 | 3
2.5361 | 14
2.5359 | 2
2.5359 | 1.5
2.5357 | 7
2.5354 | 5
2.5349 | 12.5
2.5349 | 9.5
2.5339 | 12.1
2.5339 | 10
2.5335 | 10.3
2.5327 | 18.3
2.5323 | 8.2
2.5323 | 11.3
2.5309 | 13
2.5306 | 0
2.5306 | 0
2.53 | 12.4
2.53 | 7.5
2.53 | 11.5
2.5298 | 12.1
2.5293 | 24
2.5293 | 6
2.5291 | 5
2.5291 | 6.5
2.529 | 3.85
2.529 | 2
2.5282 | 7
2.528 | 14
2.5279 | 11
2.5272 | 15.4
2.5272 | 9.7
2.527 | 7.5
2.5269 | 7
2.5268 | 14.9
2.5265 | 11
2.5265 | 10
2.5257 | 8.3
2.5251 | 19.5
2.5237 | 10.8
2.5233 | 0
2.5229 | 1
2.5225 | 3.3
2.5218 | 11.2
2.5214 | 9.7
2.5209 | 10.6
2.5202 | 8.3
2.5202 | 11
2.5196 | 9.5
2.5189 | 7.1
2.5189 | 7.4
2.5189 | 2
2.5188 | 8.5
2.5187 | 19.8
2.5182 | 2.5
2.5178 | 10.4
2.5178 | 12
2.5178 | 5.4
2.5175 | 3.3
2.5173 | 7
2.5169 | 30.4
2.5168 | 13
2.5163 | 8.9
2.5161 | 18.8
2.5161 | 5.2
2.5159 | 22
2.5153 | 4.4
2.5152 | 19
2.5149 | 16
2.5147 | 4.5
2.5147 | 2
2.5138 | 8.3
2.5133 | 4
2.5132 | 14.7
2.5131 | 10.5
2.513 | 6
2.5128 | 17
2.5124 | 11
2.5121 | 9.9
2.5121 | 8
2.512 | 1
2.512 | 8.6
2.512 | 7.1
2.5118 | 9.4
2.5117 | 4.5
2.5116 | 6.5
2.5116 | 8
2.5114 | 11
2.5113 | 8
2.5109 | 6
2.5105 | 8
2.5103 | 21
2.5103 | 5
2.5101 | 9.1
2.5099 | 22.4
2.5087 | 1
2.5083 | 21
2.5079 | 3
2.5076 | 0
2.5076 | 11.6
2.5076 | 20.1
2.5075 | 11.5
2.5075 | 23
2.5073 | 6
2.5069 | 3
2.5068 | 9.2
2.5068 | 7.4
2.5068 | 13
2.5064 | 9
2.506 | 14
2.5058 | 6.2
2.5058 | 1.1
2.5054 | 7
2.5051 | 7.9
2.5051 | 12.6
2.5047 | 9.7
2.504 | 5.1
2.504 | 25
2.5032 | 8.9
2.5027 | 9
2.5019 | 4
2.5018 | 5
2.5017 | 7
2.5017 | 4.7
2.5017 | 9.7
2.5014 | 15.7
2.5014 | 4.5
2.5003 | 11
2.5003 | 12
2.5003 | 9
2.4999 | 9.9
2.4997 | 20
2.4997 | 12.8
2.4991 | 10.7
2.499 | 5.2
2.4983 | 7.7
2.4978 | 15.1
2.4978 | 14.9
2.4974 | 10.7
2.4971 | 2
2.4969 | 14.7
2.4967 | 16
2.4967 | 10.5
2.4962 | 8
2.4962 | 10.9
2.496 | 7.4
2.496 | 11
2.496 | 17.4
2.4948 | 14.4
2.4948 | 13.3
2.4948 | 18.7
2.4941 | 30
2.4939 | 7
2.4934 | 4.5
2.4927 | 11
2.4921 | 9.8
2.492 | 6
2.492 | 5.9
2.492 | 10.5
2.492 | 15
2.4917 | 15
2.4914 | 2
2.4914 | 2
2.4906 | 23.4
2.4901 | 8
2.4899 | 16.8
2.4896 | 3.8
2.4896 | 14
2.4896 | 8.7
2.4894 | 0
2.4892 | 4
2.4892 | 8.5
2.4892 | 15.3
2.4892 | 14.7
2.4887 | 18
2.4885 | 10.7
2.4885 | 8
2.4885 | 10
2.488 | 11.9
2.488 | 1.5
2.488 | 9.2
2.4867 | 4.1
2.4865 | 2
2.486 | 12.5
2.486 | 2
2.4858 | 0
2.4852 | 9.3
2.4851 | 13.6
2.485 | 8
2.485 | 6.2
2.4847 | 11.8
2.4846 | 10.5
2.4846 | 15.2
2.4843 | 0
2.4843 | 11.3
2.4836 | 9.9
2.4828 | 8
2.4824 | 3.8
2.4824 | 12
2.4821 | 7.2
2.4818 | 6
2.4816 | 10.9
2.4815 | 11
2.4814 | 9.4
2.4814 | 0.4
2.4812 | 4.5
2.4812 | 6.6
2.4812 | 3.6
2.4808 | 22
2.4798 | 1
2.4798 | 1
2.4797 | 28
2.4796 | 0
2.4796 | 0
2.4792 | 3
2.4791 | 3.1
2.4788 | 13
2.4788 | 5
2.4788 | 16
2.4788 | 12.7
2.4788 | 11
2.4786 | 12
2.4786 | 11.5
2.4784 | 9.2
2.4784 | 21
2.4778 | 4.9
2.4778 | 18.7
2.4777 | 7.8
2.4776 | 20.1
2.4772 | 10.8
2.4771 | 14.6
2.4764 | 16
2.476 | 8
2.4757 | 7
2.4757 | 5
2.4749 | 15.5
2.4745 | 16
2.4743 | 3.9
2.4738 | 9.2
2.4737 | 7
2.4737 | 18.9
2.4731 | 11
2.4724 | 7
2.4724 | 10.4
2.4724 | 6.2
2.4723 | 10.2
2.4718 | 5.7
2.4717 | 9.2
2.4716 | 8.6
2.4716 | 9.9
2.4716 | 25
2.4712 | 6
2.471 | 8
2.471 | 7.9
2.471 | 10
2.4709 | 15.1
2.4709 | 6
2.4702 | 8.5
2.4697 | 11.4
2.4697 | 17.1
2.4695 | 5.9
2.4695 | 12.3
2.4686 | 5
2.4682 | 6.5
2.4681 | 14.5
2.468 | 6.8
2.4673 | 9
2.466 | 12
2.4654 | 7
2.4654 | 9.4
2.4654 | 0
2.4653 | 17
2.465 | 10.3
2.4647 | 2
2.4645 | 6
2.4645 | 9.5
2.4645 | 8.2
2.4645 | 16.6
2.4645 | 12
2.4643 | 2
2.4643 | 2
2.4643 | 6.5
2.4632 | 12.9
2.4632 | 4.3
2.4632 | 10.9
2.4625 | 19
2.4617 | 13.5
2.4614 | 17
2.461 | 18.5
2.4607 | 5.1
2.4606 | 4.9
2.4604 | 10.2
2.46 | 15.5
2.4597 | 14.4
2.4597 | 8.6
2.4596 | 17
2.4596 | 16.9
2.4596 | 2
2.4596 | 20
2.4595 | 15
2.4589 | 10.2
2.4588 | 10
2.4588 | 12.4
2.4582 | 16.5
2.4582 | 7
2.4578 | 0
2.4575 | 7.5
2.4575 | 11.4
2.4574 | 2
2.4572 | 10.5
2.4572 | 16.5
2.4568 | 10
2.4565 | 4.5
2.456 | 10.5
2.4555 | 12.3
2.4555 | 8.4
2.4552 | 4.2
2.4547 | 3.25
2.4545 | 9.9
2.454 | 4
2.4538 | 10
2.4535 | 7
2.4534 | 7.3
2.4531 | 16.4
2.4531 | 20.3
2.4526 | 22
2.4522 | 18.6
2.4517 | 12
2.4509 | 22.8
2.4505 | 8
2.4505 | 12
2.4505 | 14.4
2.4505 | 6.5
2.4502 | 1
2.4502 | 13
2.4502 | 18.8
2.4498 | 9.5
2.4498 | 5.4
2.4493 | 8.6
2.4491 | 19.4
2.449 | 4.9
2.449 | 10
2.449 | 8
2.4484 | 13.1
2.4483 | 7.5
2.4483 | 2.8
2.4483 | 21.2
2.447 | 26.5
2.447 | 5
2.447 | 12
2.4469 | 13.5
2.4469 | 6
2.4466 | 23
2.4466 | 13
2.4463 | 10
2.4458 | 25
2.4457 | 13
2.4454 | 4.2
2.4454 | 6
2.4447 | 11.2
2.4442 | 10.1
2.4434 | 24
2.4434 | 20
2.4432 | 0
2.443 | 5
2.443 | 1
2.443 | 12.3
2.443 | 10.4
2.4428 | 9.8
2.4427 | 13.2
2.4427 | 5.5
2.4422 | 5
2.4418 | 12
2.4418 | 9
2.4416 | 10.5
2.4415 | 0
2.4406 | 18
2.4401 | 4.7
2.4401 | 4.3
2.4401 | 6.9
2.4395 | 23
2.4385 | 14.9
2.4381 | 13.5
2.438 | 12.8
2.4378 | 9.7
2.4371 | 11
2.4371 | 10.7
2.4367 | 14.5
2.4367 | 7
2.4367 | 11.8
2.4367 | 4
2.4364 | 9.6
2.4359 | 11.3
2.4357 | 5.4
2.4353 | 3.4
2.435 | 6.8
2.435 | 8.4
2.4349 | 5.3
2.4344 | 10
2.433 | 9.8
2.4323 | 10
2.4323 | 22
2.4323 | 25
2.4322 | 11
2.4322 | 10.5
2.4322 | 5.5
2.432 | 16
2.432 | 4.1
2.4315 | 8.6
2.4313 | 2
2.4313 | 13
2.4313 | 9.5
2.4294 | 7
2.4294 | 3.5
2.4293 | 30
2.4293 | 20
2.4293 | 12.2
2.4293 | 7
2.4293 | 13
2.4287 | 19.2
2.4287 | 12
2.4286 | 10.5
2.4286 | 22
2.4285 | 3.3
2.4282 | 14.8
2.428 | 11
2.428 | 30
2.4276 | 8.4
2.4254 | 12
2.4254 | 7.7
2.4254 | 20
2.4251 | 3.3
2.425 | 9
2.4245 | 24
2.4245 | 16.5
2.4244 | 16.5
2.4243 | 8
2.4237 | 12
2.4232 | 11.5
2.423 | 8
2.423 | 1
2.4228 | 11.8
2.4223 | 9
2.4223 | 8
2.4223 | 15.9
2.4223 | 9.5
2.4222 | 6
2.4217 | 11
2.4217 | 9
2.4216 | 0
2.421 | 19
2.4209 | 3
2.4205 | 10.1
2.4205 | 9.8
2.4203 | 5.3
2.4203 | 10
2.4202 | 4.5
2.4201 | 9.8
2.4188 | 5
2.4188 | 16.2
2.4185 | 4.4
2.4181 | 8.4
2.4178 | 7.7
2.4178 | 6.3
2.4174 | 6.7
2.4167 | 14.6
2.4167 | 12.2
2.4163 | 10.4
2.416 | 14.6
2.416 | 16
2.4158 | 8
2.4156 | 5
2.4153 | 9.5
2.415 | 10.5
2.4146 | 14
2.4144 | 5.3
2.4144 | 2
2.4144 | 15
2.4143 | 9.2
2.4141 | 12.8
2.4137 | 10
2.4133 | 9
2.4132 | 10.5
2.413 | 7
2.4127 | 7.2
2.4124 | 18.4
2.4118 | 14.4
2.4108 | 9
2.4107 | 0
2.4105 | 9.5
2.4104 | 8.6
2.4103 | 11.5
2.4101 | 10.8
2.4093 | 2
2.4093 | 4.5
2.4091 | 15.7
2.409 | 8.8
2.4084 | 12
2.4084 | 16.5
2.4076 | 4.7
2.4073 | 6
2.4072 | 2
2.4072 | 1
2.4072 | 9.8
2.4069 | 10.8
2.4069 | 7
2.4062 | 3
2.4061 | 23.8
2.405 | 14
2.405 | 4.5
2.4048 | 5
2.4045 | 1
2.4036 | 14
2.4025 | 10.5
2.4025 | 10.5
2.4019 | 10
2.4019 | 8.5
2.4017 | 5
2.4014 | 9.7
2.401 | 7
2.4006 | 9.8
2.4001 | 8.1
2.4001 | 12
2.3993 | 7.8
2.3991 | 20
2.3991 | 9.8
2.3986 | 7
2.3979 | 9.3
2.3977 | 8.7
2.3977 | 5.8
2.397 | 3
2.397 | 12
2.3963 | 8.9
2.396 | 12
2.3956 | 14.6
2.3956 | 18
2.3956 | 4
2.3956 | 7
2.3954 | 17.8
2.3949 | 6.1
2.3942 | 12.2
2.3942 | 10
2.3942 | 9
2.3935 | 8.9
2.3935 | 8.3
2.3935 | 4.5
2.3935 | 10.5
2.3935 | 14
2.3929 | 3
2.3929 | 12.3
2.3928 | 10.9
2.3928 | 12
2.3915 | 11.2
2.3913 | 8
2.3909 | 20
2.3908 | 12
2.3906 | 15
2.3902 | 9
2.3901 | 4.5
2.3893 | 10
2.3893 | 22
2.3889 | 9.8
2.3889 | 15.3
2.3886 | 3.6
2.3882 | 12.5
2.3882 | 10
2.3875 | 7.2
2.3874 | 3.9
2.3872 | 1
2.3871 | 30
2.3871 | 6.5
2.3871 | 11.8
2.3871 | 11.5
2.3869 | 5.3
2.3869 | 2
2.3869 | 11.5
2.3867 | 23.4
2.3867 | 19.7
2.3867 | 0
2.3867 | 2
2.3865 | 9
2.3857 | 5.7
2.3857 | 10
2.3857 | 11
2.3854 | 1.5
2.3848 | 10.5
2.3848 | 4.5
2.3836 | 12.9
2.3835 | 8.3
2.383 | 5.4
2.383 | 12
2.3822 | 6
2.3821 | 14
2.3808 | 13.2
2.3803 | 12
2.3799 | 8.1
2.3799 | 17
2.3796 | 10.5
2.3796 | 14
2.379 | 11
2.3787 | 8.2
2.3786 | 9.8
2.3781 | 9
2.3774 | 8.5
2.3771 | 1
2.3771 | 6
2.3768 | 10
2.3767 | 14
2.3766 | 16.5
2.3759 | 21
2.3759 | 10.5
2.3752 | 10.5
2.3751 | 1
2.3751 | 15
2.3751 | 6.5
2.3741 | 3
2.3734 | 11.5
2.373 | 24
2.373 | 0
2.3725 | 8.7
2.3724 | 9
2.3724 | 9.5
2.3723 | 5.4
2.3723 | 9.7
2.3723 | 11
2.3719 | 11
2.3719 | 11
2.3717 | 5
2.3716 | 7
2.3714 | 5.9
2.3714 | 9
2.3703 | 9
2.3703 | 1
2.3699 | 4
2.3696 | 3.7
2.3694 | 11.2
2.3693 | 12.5
2.3688 | 15
2.3687 | 16
2.3687 | 16.6
2.368 | 19
2.368 | 12
2.3673 | 7
2.3672 | 7.8
2.3672 | 8
2.3668 | 6
2.3667 | 7.4
2.366 | 8
2.3654 | 10.7
2.3654 | 8
2.3654 | 4.5
2.3653 | 15.5
2.365 | 3
2.3647 | 9
2.3635 | 2.6
2.3635 | 1
2.3633 | 6
2.3627 | 19
2.3626 | 8
2.3619 | 13.8
2.3614 | 10.4
2.3614 | 4
2.3614 | 8
2.3614 | 9.7
2.3607 | 18
2.3607 | 5.5
2.3605 | 8
2.3594 | 9
2.3592 | 10.4
2.3588 | 30.7
2.3585 | 9.7
2.3583 | 9
2.3572 | 7.2
2.3572 | 10
2.3571 | 14
2.3569 | 9.5
2.3566 | 9
2.3552 | 3.3
2.3552 | 10.6
2.3548 | 10
2.3548 | 7
2.3546 | 16
2.3542 | 5.9
2.3519 | 9.5
2.3519 | 13.8
2.3519 | 10
2.3511 | 1.5
2.3505 | 10
2.3505 | 16
2.3499 | 3
2.3499 | 10
2.3499 | 16
2.3499 | 8
2.3499 | 9.6
2.3499 | 9.7
2.3499 | 11
2.3498 | 20
2.3496 | 4.4
2.3485 | 15.6
2.3484 | 16.3
2.3477 | 7
2.3477 | 10.4
2.3477 | 15.2
2.3477 | 17
2.347 | 13
2.345 | 6.2
2.3447 | 14
2.3444 | 9
2.3443 | 4.6
2.3443 | 3
2.3438 | 8.5
2.3422 | 0
2.3415 | 17
2.3414 | 14.2
2.3414 | 6
2.3409 | 10.5
2.3409 | 10.5
2.3404 | 15.5
2.3393 | 8.2
2.3383 | 6
2.3377 | 9
2.3374 | 16.2
2.337 | 11
2.337 | 10.5
2.3365 | 8.4
2.3359 | 7
2.3356 | 2.5
2.3356 | 5
2.3352 | 25.3
2.3351 | 9.9
2.3351 | 17
2.335 | 11.9
2.3349 | 8.8
2.3343 | 4.2
2.3343 | 6.1
2.334 | 8.2
2.3337 | 10.2
2.3323 | 9.4
2.332 | 10
2.332 | 10
2.3313 | 11.5
2.3313 | 5.8
2.3311 | 10.5
2.331 | 3.6
2.3308 | 8.2
2.3308 | 7.5
2.3307 | 20
2.3306 | 7.6
2.3302 | 9
2.329 | 13.5
2.3289 | 4.5
2.3285 | 0
2.3284 | 12.8
2.3284 | 8.1
2.328 | 12.4
2.3276 | 5.3
2.3249 | 10
2.3248 | 21.2
2.3244 | 3.1
2.3242 | 15.7
2.3242 | 6
2.3238 | 9
2.3236 | 10.6
2.3235 | 9.5
2.3224 | 10.2
2.3217 | 12.5
2.3214 | 10.8
2.3213 | 13
2.321 | 8.5
2.3209 | 12
2.3206 | 8.5
2.3206 | 8.2
2.3203 | 9.2
2.3203 | 9
2.3184 | 10
2.3183 | 5.8
2.3182 | 10.6
2.3176 | 15
2.3176 | 6.1
2.3175 | 6.2
2.3169 | 4.9
2.3168 | 11.5
2.3167 | 33
2.3167 | 13.2
2.3162 | 8.4
2.3156 | 13.7
2.3153 | 3.6
2.315 | 7.6
2.315 | 9.5
2.315 | 5
2.3148 | 8.3
2.3148 | 14.3
2.3141 | 4
2.3141 | 12
2.3141 | 8.7
2.3141 | 7.9
2.3137 | 6
2.3137 | 8
2.3135 | 16.5
2.3135 | 2.9
2.3135 | 4
2.3124 | 17
2.3121 | 6.5
2.3119 | 8.6
2.3114 | 0
2.3105 | 16
2.3104 | 5
2.3101 | 7.7
2.3101 | 6.2
2.3094 | 10.4
2.3094 | 6.9
2.3094 | 14.2
2.3091 | 9
2.3084 | 12.2
2.3084 | 8.5
2.3074 | 13.5
2.3074 | 18
2.3074 | 18.4
2.307 | 16.9
2.307 | 5
2.3066 | 7
2.3056 | 10
2.3049 | 7
2.3049 | 8.4
2.3046 | 3.3
2.304 | 17.1
2.3039 | 0
2.3034 | 10
2.3034 | 10
2.3014 | 8
2.3007 | 16.5
2.3007 | 12
2.3006 | 10
2.3006 | 21
2.2998 | 6.5
2.2986 | 12.4
2.298 | 5
2.298 | 16
2.2973 | 9
2.2966 | 10.3
2.2966 | 10
2.2966 | 19
2.2964 | 12.9
2.2956 | 8.5
2.2955 | 5.4
2.295 | 9
2.2942 | 10
2.2935 | 3
2.2933 | 6.7
2.2933 | 17
2.293 | 11
2.2926 | 5
2.2926 | 12.5
2.2921 | 1
2.2921 | 10.9
2.2919 | 8.7
2.2915 | 9
2.2908 | 2
2.29 | 6.5
2.2899 | 12
2.288 | 9
2.2875 | 10
2.2869 | 10.7
2.2856 | 12
2.2856 | 8.4
2.2849 | 26
2.2843 | 21.3
2.2843 | 9
2.2832 | 0.2
2.2832 | 13.7
2.2832 | 9.5
2.283 | 3
2.2827 | 4.4
2.2827 | 3.9
2.2823 | 14.3
2.2823 | 9.2
2.2823 | 10.2
2.282 | 6
2.2819 | 15
2.2816 | 3.9
2.2816 | 8.4
2.2809 | 9
2.2805 | 10
2.2802 | 7.8
2.2793 | 15.5
2.279 | 2
2.279 | 10.8
2.279 | 5
2.2777 | 10
2.2771 | 4.2
2.2771 | 7
2.2764 | 21
2.2764 | 10
2.2758 | 3
2.2751 | 20.5
2.2739 | 8
2.2737 | 16.7
2.2737 | 10
2.2731 | 8.5
2.2718 | 16
2.2712 | 5.9
2.2704 | 4.8
2.2704 | 5
2.2704 | 4.9
2.2697 | 14.2
2.269 | 8.4
2.269 | 5.9
2.269 | 12
2.2676 | 10
2.2676 | 21
2.2657 | 12.2
2.2657 | 16
2.2648 | 10
2.2647 | 4
2.2632 | 4.9
2.2627 | 3.3
2.2627 | 9.5
2.262 | 11
2.2619 | 6.5
2.2614 | 7
2.261 | 12.5
2.2604 | 11
2.2604 | 8.1
2.2603 | 10.7
2.2594 | 4.5
2.2591 | 7
2.2587 | 14
2.2581 | 8
2.2569 | 8.4
2.2567 | 6.5
2.2562 | 9
2.2553 | 4.8
2.2535 | 4.5
2.2535 | 8
2.2535 | 7.2
2.2532 | 17
2.2529 | 21.3
2.2529 | 13
2.2516 | 6.9
2.2511 | 10.9
2.2501 | 8.2
2.2495 | 9
2.249 | 20
2.249 | 9.5
2.249 | 16
2.249 | 16
2.2488 | 0
2.2486 | 12.9
2.2478 | 8.4
2.2472 | 14
2.2468 | 10
2.2464 | 9
2.2464 | 8.6
2.245 | 13.2
2.245 | 10
2.2437 | 6.5
2.2423 | 4.1
2.2421 | 11.5
2.2418 | 5.3
2.2398 | 5
2.2398 | 5
2.2392 | 21.9
2.2392 | 6
2.2387 | 8.5
2.2387 | 8
2.2385 | 18.1
2.2382 | 7.6
2.2372 | 8
2.2372 | 25.3
2.2368 | 6.5
2.2366 | 6.8
2.236 | 17.5
2.236 | 22
2.2354 | 10.7
2.2348 | 5.4
2.2337 | 7
2.2333 | 4.5
2.2333 | 4.5
2.2333 | 4.5
2.2333 | 12
2.2328 | 6
2.232 | 7.2
2.2313 | 13.4
2.2303 | 11
2.2294 | 4
2.2293 | 9
2.2279 | 4.2
2.2268 | 12
2.2267 | 1
2.2266 | 4
2.2266 | 5
2.2266 | 9.2
2.2261 | 23
2.226 | 26
2.2235 | 12.3
2.2228 | 3
2.2226 | 6.7
2.2224 | 10
2.2219 | 0
2.2211 | 11.1
2.2209 | 26.5
2.2203 | 10
2.2199 | 14.3
2.2192 | 7
2.2177 | 15
2.2177 | 9
2.2166 | 1
2.2166 | 10.7
2.2165 | 17.6
2.2165 | 19
2.2163 | 17
2.2158 | 9
2.2152 | 6
2.2137 | 1
2.2137 | 12
2.2137 | 12
2.2131 | 4.5
2.213 | 11
2.2125 | 5.5
2.2125 | 18
2.2125 | 20
2.2123 | 10.8
2.2117 | 7
2.2108 | 15
2.2104 | 3.9
2.2104 | 14.1
2.2098 | 20
2.2094 | 7
2.2093 | 10.7
2.2091 | 9
2.2091 | 9
2.2084 | 5.7
2.2084 | 16
2.2067 | 10
2.2064 | 10
2.2064 | 10
2.2057 | 7.4
2.2052 | 7
2.2032 | 19
2.2026 | 9.5
2.2017 | 16
2.2006 | 12.4
2.2005 | 5.2
2.2 | 6
2.2 | 16
2.1993 | 4
2.199 | 6.5
2.1986 | 11.5
2.1981 | 21
2.1973 | 9.5
2.1971 | 13
2.196 | 7
2.195 | 16
2.195 | 0
2.1933 | 8.7
2.1929 | 5.8
2.1915 | 24.5
2.1912 | 0
2.1904 | 10.8
2.1903 | 15.5
2.1875 | 12.4
2.1862 | 5.8
2.1862 | 4
2.1862 | 7
2.1861 | 14
2.1843 | 8.4
2.1836 | 15
2.183 | 8
2.183 | 10
2.181 | 9
2.181 | 13
2.181 | 5
2.1803 | 7
2.18 | 6.8
2.1797 | 9
2.1797 | 8
2.1797 | 9.4
2.1759 | 10.8
2.1754 | 9
2.1738 | 7
2.1732 | 7.8
2.1732 | 19
2.1732 | 6.2
2.1709 | 10
2.1701 | 12
2.1694 | 6
2.1686 | 13
2.1679 | 9
2.1673 | 10.5
2.166 | 7
2.1642 | 7
2.1633 | 4
2.1628 | 13
2.1621 | 0
2.1614 | 8
2.1607 | 10.5
2.1601 | 22
2.1594 | 10
2.1593 | 4.6
2.1581 | 8.4
2.1561 | 4
2.1552 | 12.3
2.1549 | 12
2.1549 | 5
2.1549 | 5
2.1542 | 9.5
2.1542 | 8
2.1525 | 4
2.1509 | 4
2.1509 | 4
2.1503 | 9.5
2.1499 | 4.5
2.1492 | 7.5
2.1487 | 7.5
2.1485 | 10.5
2.1477 | 13
2.147 | 10
2.147 | 4
2.1465 | 7
2.1439 | 0
2.1424 | 19.3
2.1405 | 4
2.1403 | 4.5
2.1391 | 15.7
2.1391 | 11.1
2.1391 | 5
2.1386 | 22
2.1385 | 12.5
2.1379 | 13
2.1355 | 8.7
2.1352 | 12.4
2.1352 | 8.4
2.1339 | 9.8
2.1293 | 10.7
2.1287 | 7.5
2.1281 | 6
2.1274 | 9.5
2.1274 | 18.1
2.1222 | 12.4
2.1215 | 10
2.1209 | 16
2.1209 | 21
2.1206 | 7
2.1183 | 3.8
2.1183 | 3.5
2.1148 | 11.5
2.1121 | 4.7
2.1119 | 13.2
2.1111 | 4
2.1084 | 4
2.1074 | 16
2.1054 | 5
2.1045 | 9.6
2.1013 | 18.3
2.0959 | 10.8
2.0953 | 4.1
2.0915 | 8.5
2.0914 | 6.4
2.09 | 11.8
2.0882 | 9
2.0852 | 4.5
2.0849 | 8
2.0849 | 20
2.0805 | 0
2.0785 | 5
2.077 | 8.2
2.0769 | 13.9
2.0758 | 9
2.0742 | 23
2.0742 | 22
2.0739 | 7
2.0698 | 8
2.0639 | 10.7
2.062 | 9
2.062 | 20
2.0616 | 18
2.0588 | 9.4
2.0568 | 19.1
2.0562 | 10.3
2.0549 | 18.3
2.0529 | 10
2.0522 | 9.8
2.049 | 9
2.0478 | 7.5
2.0464 | 4
2.0431 | 14.2
2.0401 | 15.6
2.0397 | 18
2.0359 | 7
2.0294 | 18.2
2.0196 | 7
2.0196 | 9.8
2.0192 | 19.8
2.0163 | 11.2
2.0157 | 20.3
2.0129 | 0
2.0104 | 9
2.0104 | 4
2.0104 | 4
2.0044 | 5
2.0042 | 7.5
2.0032 | 7
1.9986 | 18.9
1.9973 | 9.6
1.9969 | 6.8
1.9952 | 16.6
1.9869 | 7
1.9843 | 11.4
1.9647 | 11.7
1.9613 | 14
1.9576 | 13.8
1.9467 | 14.4
1.5145 | 13.2

## Transformadores (hidden)
Alternative | Capacity (MVA) | Impedance (Ohmios) | C. Mant ($) | C. Inver ($) |  |  | C. Prod ($) |  |  | Coste Fijo ($) | VB | 13800
Exist | 12 | 0.16 | 2000 | - |  | B1 | 57.7 |  | SS1 | 100000 | SB | 1000000
1 | 7.5 | 0.25 | 1000 | 500000 |  | B2 | 70 |  | SS2 | 100000 | pf | 0.9
2 | 15 | 0.13 | 3000 | 950000 |  | B3 | 85.3 |  | SS3 | 150000
PARAMETRO A DE LINEALIZACION
| EXIST.1 | EXIST.2 | EXIST.3 | 1.1 | 1.2 | 1.3 | 2.1 | 2.2 | 2.3
S1 | 3 | 6.6 | 12 | 1.875 | 4.125 | 7.5 | 3.75 | 8.25 | 15
S2 | 3 | 6.6 | 12 | 1.875 | 4.125 | 7.5 | 3.75 | 8.25 | 15
S3 | 0 | 0 | 0 | 1.875 | 4.125 | 7.5 | 3.75 | 8.25 | 15
PARAMETRO B DE LINEALIZACION
| EXIST.1 | EXIST.2 | EXIST.3 | 1.1 | 1.2 | 1.3 | 2.1 | 2.2 | 2.3
S1 | 0.0068053 | 0.032938 | 0.10888 | 0.0041536 | 0.020104 | 0.066458 | 0.0086395 | 0.041815 | 0.13823
S2 | 0.0068053 | 0.032938 | 0.10888 | 0.0041536 | 0.020104 | 0.066458 | 0.0086395 | 0.041815 | 0.13823
S3 | 0 | 0 | 0 | 0.0041536 | 0.020104 | 0.066458 | 0.0086395 | 0.041815 | 0.13823
RESISTENCIA TRANSFORMADORES | bar: EXIST.1 to EXIST.3
| EXIST | 1 | 2
S1 | EXIST.1: 0.00075614; EXIST.2: 0.0011815; EXIST.3: 0.00061437
S2 | EXIST.1: 0.00075614; EXIST.2: 0.0011815; EXIST.3: 0.00061437
S3 | EXIST.1: 0; EXIST.2: 0.0011815; EXIST.3: 0.00061437

## Distributed Generation (hidden)
DG alternative | Conventional |  |  | Wind
| Capacity (MVA) | C. Inver ($/MVA) | C. Produc ($/MVAh) | Capacity (MVA) | C. Inver ($/MVA) | C. Produc ($/MVAh)
1 | 1 | 500000 | 52 | 0.91 | 1750000 | 0
2 | 2 | 490000 | 50 | 2.05 | 1740000 | 0

## Nudos Candidatos (hidden)
Nudos GC | Nudos Zonas eólicas
| A | B | C
10 | 31 | 94 | 78
28 | 52 | 103 | 116
38 | 113 | 120
53 | 114
64 | 122
94
108
117
126
133

## Hoja1 (hidden)
Node | Stage
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 122 | 126 | 129 | 133 | 137 | 140 | 144 | 148 | 151 | 155 | 242 | 246 | 249 | 253 | 257 | 260 | 264 | 268 | 271 | 275
2 | 45 | 46 | 48 | 49 | 50 | 52 | 53 | 54 | 56 | 57 | 165 | 166 | 168 | 169 | 170 | 172 | 173 | 174 | 176 | 177
3 | 74 | 76 | 78 | 81 | 83 | 85 | 87 | 90 | 92 | 94 | 194 | 196 | 198 | 201 | 203 | 205 | 207 | 210 | 212 | 214
4 | 80 | 82 | 85 | 87 | 90 | 92 | 94 | 97 | 99 | 102 | 200 | 202 | 205 | 207 | 210 | 212 | 214 | 217 | 219 | 222
5 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 44 | 45 | 46 | 156 | 157 | 158 | 159 | 160 | 161 | 162 | 164 | 165 | 166
6 | 74 | 76 | 78 | 81 | 83 | 85 | 87 | 90 | 92 | 94 | 194 | 196 | 198 | 201 | 203 | 205 | 207 | 210 | 212 | 214
7 | 137 | 141 | 145 | 149 | 153 | 158 | 162 | 166 | 170 | 174 | 257 | 261 | 265 | 269 | 273 | 278 | 282 | 286 | 290 | 294
8 | 143 | 147 | 152 | 156 | 160 | 164 | 169 | 173 | 177 | 182 | 263 | 267 | 272 | 276 | 280 | 284 | 289 | 293 | 297 | 302
9 | 40 | 41 | 42 | 44 | 45 | 46 | 47 | 48 | 50 | 51 | 160 | 161 | 162 | 164 | 165 | 166 | 167 | 168 | 170 | 171
10 | 125 | 129 | 133 | 136 | 140 | 144 | 148 | 151 | 155 | 159 | 245 | 249 | 253 | 256 | 260 | 264 | 268 | 271 | 275 | 279
11 | 69 | 71 | 73 | 75 | 77 | 79 | 81 | 83 | 86 | 88 | 189 | 191 | 193 | 195 | 197 | 199 | 201 | 203 | 206 | 208
12 | 110 | 113 | 117 | 120 | 123 | 127 | 130 | 133 | 136 | 140 | 230 | 233 | 237 | 240 | 243 | 247 | 250 | 253 | 256 | 260
13 | 146 | 150 | 155 | 159 | 164 | 168 | 172 | 177 | 181 | 185 | 266 | 270 | 275 | 279 | 284 | 288 | 292 | 297 | 301 | 305
14 | 144 | 148 | 153 | 157 | 161 | 166 | 170 | 174 | 179 | 183 | 264 | 268 | 273 | 277 | 281 | 286 | 290 | 294 | 299 | 303
15 | 16 | 16 | 17 | 17 | 18 | 18 | 19 | 19 | 20 | 20 | 136 | 136 | 137 | 137 | 138 | 138 | 139 | 139 | 140 | 140
16 | 26 | 27 | 28 | 28 | 29 | 30 | 31 | 31 | 32 | 33 | 146 | 147 | 148 | 148 | 149 | 150 | 151 | 151 | 152 | 153
17 | 131 | 135 | 139 | 143 | 147 | 151 | 155 | 159 | 162 | 166 | 251 | 255 | 259 | 263 | 267 | 271 | 275 | 279 | 282 | 286
18 | 103 | 106 | 109 | 112 | 115 | 118 | 122 | 125 | 128 | 131 | 223 | 226 | 229 | 232 | 235 | 238 | 242 | 245 | 248 | 251
19 | 19 | 20 | 20 | 21 | 21 | 22 | 22 | 23 | 24 | 24 | 139 | 140 | 140 | 141 | 141 | 142 | 142 | 143 | 144 | 144
20 | 0 | 93 | 96 | 99 | 101 | 104 | 107 | 110 | 113 | 115 | 0 | 213 | 216 | 219 | 221 | 224 | 227 | 230 | 233 | 235
21 | 0 | 16 | 16 | 17 | 17 | 18 | 18 | 19 | 19 | 20 | 0 | 136 | 136 | 137 | 137 | 138 | 138 | 139 | 139 | 140
22 | 0 | 82 | 84 | 87 | 89 | 92 | 94 | 97 | 99 | 102 | 0 | 202 | 204 | 207 | 209 | 212 | 214 | 217 | 219 | 222
23 | 0 | 0 | 83 | 85 | 88 | 90 | 93 | 95 | 98 | 100 | 0 | 0 | 203 | 205 | 208 | 210 | 213 | 215 | 218 | 220
24 | 0 | 0 | 80 | 82 | 85 | 87 | 90 | 92 | 94 | 97 | 0 | 0 | 200 | 202 | 205 | 207 | 210 | 212 | 214 | 217
25 | 0 | 0 | 92 | 95 | 98 | 100 | 103 | 106 | 109 | 111 | 0 | 0 | 212 | 215 | 218 | 220 | 223 | 226 | 229 | 231
26 | 0 | 0 | 0 | 64 | 66 | 68 | 70 | 72 | 74 | 76 | 0 | 0 | 0 | 184 | 186 | 188 | 190 | 192 | 194 | 196
27 | 0 | 0 | 0 | 62 | 64 | 66 | 68 | 69 | 71 | 73 | 0 | 0 | 0 | 182 | 184 | 186 | 188 | 189 | 191 | 193
28 | 0 | 0 | 0 | 128 | 132 | 136 | 140 | 143 | 147 | 151 | 0 | 0 | 0 | 248 | 252 | 256 | 260 | 263 | 267 | 271
29 | 0 | 0 | 0 | 0 | 68 | 70 | 72 | 74 | 76 | 78 | 0 | 0 | 0 | 0 | 188 | 190 | 192 | 194 | 196 | 198
30 | 0 | 0 | 0 | 0 | 89 | 92 | 94 | 97 | 100 | 102 | 0 | 0 | 0 | 0 | 209 | 212 | 214 | 217 | 220 | 222
31 | 0 | 0 | 0 | 0 | 42 | 43 | 45 | 46 | 47 | 48 | 0 | 0 | 0 | 0 | 162 | 163 | 165 | 166 | 167 | 168
32 | 0 | 0 | 0 | 0 | 129 | 133 | 137 | 141 | 144 | 148 | 0 | 0 | 0 | 0 | 249 | 253 | 257 | 261 | 264 | 268
33 | 0 | 0 | 0 | 0 | 0 | 112 | 115 | 119 | 122 | 125 | 0 | 0 | 0 | 0 | 0 | 232 | 235 | 239 | 242 | 245
34 | 0 | 0 | 0 | 0 | 0 | 71 | 73 | 75 | 77 | 80 | 0 | 0 | 0 | 0 | 0 | 191 | 193 | 195 | 197 | 200
35 | 0 | 0 | 0 | 0 | 0 | 134 | 138 | 142 | 146 | 150 | 0 | 0 | 0 | 0 | 0 | 254 | 258 | 262 | 266 | 270
36 | 0 | 0 | 0 | 0 | 0 | 123 | 127 | 130 | 134 | 138 | 0 | 0 | 0 | 0 | 0 | 243 | 247 | 250 | 254 | 258
37 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 101 | 104 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 221 | 224 | 227
38 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 95 | 98 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 212 | 215 | 218 | 220
39 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 44 | 46 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 164 | 166 | 167
40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 101 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 218 | 221 | 224
41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 14 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 134 | 134 | 135
42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 126 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 242 | 246 | 249
43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 148 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 268 | 273
44 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 269 | 273
45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 216
46 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 228
47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 137 | 138
48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 207
49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 221
50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243

## Branch Lengths (km)
Branch Lengths (km)
From | to | Lenght
1 | 2 | 0.655
1 | 9 | 0.864
1 | 51 | 1.105
3 | 4 | 0.899
3 | 51 | 2.057
4 | 5 | 1.451
4 | 7 | 1.24
5 | 6 | 0.813
6 | 28 | 1.549
7 | 8 | 1.004
8 | 25 | 0.793
8 | 27 | 1.595
8 | 33 | 1.923
9 | 17 | 1.611
9 | 22 | 2.08
9 | 23 | 1.363
10 | 23 | 1.885
10 | 31 | 0.917
11 | 12 | 1.417
11 | 52 | 1.504
12 | 13 | 1.701
12 | 45 | 1.331
13 | 43 | 1.072
14 | 15 | 1.805
14 | 46 | 1.31
14 | 50 | 2.247
14 | 52 | 2.212
15 | 16 | 0.91
16 | 40 | 1.29
17 | 18 | 1.831
18 | 19 | 0.68
18 | 21 | 0.984
19 | 20 | 0.962
21 | 54 | 0.578
22 | 23 | 1.85
22 | 54 | 1.886
23 | 24 | 0.82
24 | 25 | 0.894
26 | 27 | 0.68
27 | 28 | 1.145
28 | 53 | 1.635
29 | 30 | 1.165
30 | 43 | 1.465
30 | 54 | 1.02
31 | 37 | 0.447
32 | 39 | 1.458
33 | 34 | 0.813
33 | 39 | 1.193
34 | 35 | 0.76
35 | 36 | 0.446
36 | 53 | 1.28
37 | 43 | 1.008
38 | 39 | 1.19
38 | 44 | 1.274
40 | 41 | 1.387
41 | 42 | 1.522
41 | 53 | 1.734
42 | 47 | 1.82
42 | 48 | 1.77
44 | 45 | 1.018
46 | 47 | 1.29
48 | 49 | 1.576
49 | 50 | 0.918

## Data for Conductors
Branches with switchable feeder under normal operation | 10-31, 13-43, 23-24, 33-39, and 38-44 | Data for Candidate Conductors
Upper limit of existing feeders (MVA) | 6.28 | Type | Alternative 1 |  |  | Alternative 2
Impedance of existing feeders (Ω/km) | 0.557 | l | Upper limit | Impedance | Investment cost | Upper limit | Impedance | Investment cost
Maintenace cost of all feeders ($/year) | 450 |  | (MVA) | (Ω/km) | ($/km) | (MVA) | (Ω/km) | ($/km)
Lifetime of all feeders (year) | 25 | NRF | 9 | 0.478 | 19140 | 12 | 0.423 | 29870
Failure rates per year of all feeders | 0.4 | NAF | 6.28 | 0.557 | 15020 | 9 | 0.478 | 25030
Interruption duration for repair (h) | 2
Interruption duration for switching (h) | 0.25

## Data for Substations
Voltage at substation nodes (pu) |  | 1.05 | Data for Candidate Transformers
Upper limit for transformer of existing substations (MVA) |  | 12 | Alternative 1 |  |  |  | Alternative 2
Impedance of transformer of existing substations (Ω) |  | 0.16 | Upper limit | Impedance | Maintenance cost | Investment cost | Upper limit | Impedance | Maintenance cost | Investment cost
Maintenance cost of transformer of existing substations ($) |  | 2000 | (MVA) | (Ω) | ($) | ($) | (MVA) | (Ω) | ($) | ($)
Cost of unserved energy ($/MWh) |  | 1000 | 12 | 0.16 | 2000 | 750000 | 15 | 0.13 | 3000 | 950000
Lifetime of all transformers (year) |  | 15
Lifetime of all substation assets other than transformers (year) |  | ∞
Expansion costs of substations ($) | Node 51 | 100000
| Node 52 | 100000
| Node 53 | 150000
| Node 54 | 150000
Cost of energy supplied by all substation ($/MWh)* | Time block 1 | 225.33
| Time block 2 | 182.72
| Time block 3 | 154.43
| Time block 4 | 81.62
*These costs are based on the cost data reported in "http://www.esios.ree.es/web-publica/" for the Canary Islands, Spain.

## Data for DG units
Penetration limit (%) | 25 | Data for Candidate DG Units*
Candidate nodes for wind generators | 3, 15, 23, 35, and 42 |  | Wind generators |  |  | Photovoltaic generators
Candidate nodes for photovoltaic generators | 4, 12, 24, 36, and 43 | Alternative | Rated capacity | Investment cost | Cost of energy supplied | Rated capacity | Investment cost | Cost of energy supplied
Maintenance costs for generators | 5% of investment cost | k | (MVA) | ($/MW) | ($/MWh) | (MVA) | ($/MW) | ($/MWh)
Lifetime of allgenerators (year) | 20 | 1 | 0.91 | 185000 | 0 | 0.7 | 172000 | 0
|  | 2 | 2.05 | 184000 | 0 | 1.65 | 171000 | 0
*Wind generation limits associated with the wind speed levels are determined using the data available in "http://www.enercon.de/fileadmin/Redakteur/Medien-Portal/broschueren/pdf/en/ENERCON_Produkt_en_06_2015.pdf" related to wind generators E44 and E82, which correspond to alternatives 1 and 2, respectively. Photovoltaic generation limits associated with the solar irradiation levels are determined using the data available in "http://www.kyocerasolar.com/commercial-solutions/solar-panels/current-products.htm" related to 5000 solar panels of types KD100-36 and KD300-80 within F Series, which correspond to alternatives 1 and 2, respectively.

## Reliability data
Penatly factor χ | 20
Penalty factor ς | 0.01
Target for the customer interruption duration (h/yr) | 4
Target for the customer interruption frequency (Interruptions per year) | 4
Target for the system average interruption duration (h/yr) | 2.5
Target for the system average interruption frequency (Interruptions per year) | 2.5